## Capacity
Discount Rate | 7.24% |  |  |  |  | NorthWestern will include the protocal for each year in order to calcualte accredited capacity. The curren protocal from 2016 is below:
Escalation Rate | 2% |  |  |  |  | Market Protocols for SPP Integrated Marketplace
Nameplate Capacity | 60 |  |  |  |  | 4.1.2.2 Wind-Powered Generation Resource Output Forecasts
Capacity Contribution | 5% |  |  |  |  | 4.1.2.3 Wind-Powered Generation Resource Data Requirements
Capacity credit | 3 |  |  |  |  | SPP Planning Criteria Version 1, 11/20/2015, 7.1.5.3 (7)
The recommended methodology to evaluate the net planning capability established for wind or solar facilities shall be determined on a monthly basis, as stated below. If a member's desire to use a more restrictive methodology to evalutate the net capabitlity of wind or solar they may do so, however net capability determined by the alternative methodology employed cannot credit the wind or solar with a capability greater than determined with the methodology stated below:
|  | Yearly Price/MW | Credited Capacity Per Project | Avoided Cost for Each Project Per year | 3 Projects |  | a. Assemble all available hourly net power output (MWH) data measured at the system interconnection point.
Capacity Value | 2019 | 117778.7146 | 1 | 117778.7146 | 353336.1437 |  | b. Select the hourly net power output values occurring during the top 3% of load hours for the SPP Load Serving Entity for each month of each year for the evaluation period
| 2020 | 117909.6889 | 1 | 117909.6889 | 353729.0666 |  | c. Select the hourly net power output value that can be expected from the facility 60% of the time or greater. For example, for a 5 year period with the 110 hourly net power output values ranked from the highest to lowest, the capacity of the facility will be the MW value in the 65th data point.
| 2021 | 118043.2826 | 1 | 118043.2826 | 354129.8479 |  | d. A seasonal or annual net capability may be determined by selecting the appropriate monthly MW values corresponding to the Load Serving Entity’s peak load month of the season of interest (e.g., 22 hours for a typical 30 day month and 110 hours for a 5 year period).
| 2022 | 118179.5483 | 1 | TBD | TBD |  | e. Facilities in commercial operation 3 years or less:
| 2023 | 118318.5393 | 1 | TBD | TBD |  |  | i. The data must include the most recent 3 years.
| 2024 | 118460.31 | 1 | TBD | TBD |  | f. Values may be calculated from wind or solar data, if measured MW values are not yet available. Wind data correlated with a reference tower beyond fifty miles is subject to Generation Working Group approval. Solar data correlated with a reference measuring device beyond two hundred miles is subject to Generation Working Group approval. For calculated values, at least one year must be based on site specific data.
| 2025 | 118604.9162 | 1 | TBD | TBD |  | g. If the Load Serving Entity chooses not to perform the net capability calculations as described above during the first 3 years of commercial operation, the Load Serving Entity may submit 5% for wind facilities and 10% for solar facilities of the site facility’s nameplate rating.
| 2026 | 118752.4146 | 1 | TBD | TBD |  | h. Facilities in commercial operation 4 years and greater:
| 2027 | 118902.8629 | 1 | TBD | TBD |  |  | i. The data must include all available data up to the most recent 10 years of commercial operation.
| 2028 | 119056.3201 | 1 | TBD | TBD |  |  | ii. Only metered hourly net power output (MWH) data may be used.
| 2029 | 119212.8465 | 1 | TBD | TBD |  |  | iii. After three years of commercial operations, if the Load Serving Entity does not perform or provide the net capability calculations to SPP as described above, then the net capability for the resource will be 0 MW.
| 2030 | 119372.5034 | 1 | TBD | TBD |  | i. The net capability calculation shall be updated at least once every three years.
| 2031 | 119535.3535 | 1 | TBD | TBD
| 2032 | 119701.4606 | 1 | TBD | TBD
| 2033 | 119870.8898 | 1 | TBD | TBD
| 2034 | 120043.7076 | 1 | TBD | TBD
| 2035 | 120219.9817 | 1 | TBD | TBD
| 2036 | 120399.7814 | 1 | TBD | TBD
| 2037 | 120583.177 | 1 | TBD | TBD
| 2038 | 120770.2405 | 1 | TBD | TBD
|  | Levelized Cost per kW-yr | Fixed O&M/kW-yr | Total $/kW-yr
1 | 2019 | 111.23 | 6.5487 | 117.7787 |  | $111.23 - Levelized cost for Aero CT built in 2018
2 | 2020 | 111.23 | 6.6797 | 117.9097 |  | $6.55 - Fixed O&M per kW in 2018, escalating at 2%
3 | 2021 | 111.23 | 6.8133 | 118.0433
4 | 2022 | 111.23 | 6.9495 | 118.1795
5 | 2023 | 111.23 | 7.0885 | 118.3185
6 | 2024 | 111.23 | 7.2303 | 118.4603
7 | 2025 | 111.23 | 7.3749 | 118.6049
8 | 2026 | 111.23 | 7.5224 | 118.7524
9 | 2027 | 111.23 | 7.6729 | 118.9029
10 | 2028 | 111.23 | 7.8263 | 119.0563
11 | 2029 | 111.23 | 7.9828 | 119.2128
12 | 2030 | 111.23 | 8.1425 | 119.3725
13 | 2031 | 111.23 | 8.3054 | 119.5354
14 | 2032 | 111.23 | 8.4715 | 119.7015
15 | 2033 | 111.23 | 8.6409 | 119.8709
16 | 2034 | 111.23 | 8.8137 | 120.0437
17 | 2035 | 111.23 | 8.99 | 120.22
18 | 2036 | 111.23 | 9.1698 | 120.3998
19 | 2037 | 111.23 | 9.3532 | 120.5832
20 | 2038 | 111.23 | 9.5402 | 120.7702
|  |  | Levelized | 118.84

## Avoided Cost Energy
WACC | 7.24% | nominal, annual | [10 empty] | Information Only
Total Avoided Cost
NPV and Annualized Energy Costs $/MWh | [12 empty] | Levelized Payment
NPV Of Energy Costs | 82130168.3258 | [11 empty] | 25.7241
Levelized Payment | 28.4922
Total Avoided Cost
Summary Table: Annual Wind QF Generation and Avoided Costs | [12 empty] | Offer Price
Year | Generation (MWh) | Generation offsetting internal production (MWh) | Offset Purchases (MWh) | Average Offsetting Generation Avoided Cost ($/MWh) | Average Offset Purchase Price ($/MWh) | Total Offsetting Generation Avoided Cost ($) | Total Avoided Cost of Purchases ($) | Total Avoided Cost ($) | Average Avoided Cost ($/MWh) | REC Value | Regulation | Interconnection Upgrade Costs | Average Avoided Cost ($/MWh) With RECs
2017 | 277155.846 | 125955.1497 | 151200.6964 | 16.8325 | 22.4526 | 2120143.9016 | 3394856.1194 | 5515000.021 | 19.8986 | 0.37 | -0.32163 | -2.8406 | 17.1064
2018 | 277190.1684 | 106838.0077 | 170352.1607 | 15.6822 | 22.1207 | 1675451.9412 | 3768300.8676 | 5443752.8088 | 19.6391 | 0.40439 | -0.35152 | -2.8406 | 16.8514
2019 | 277190.1234 | 94385.0885 | 182805.0349 | 16.9718 | 24.2742 | 1601882.4739 | 4437440.3332 | 6039322.807 | 21.7877 | 0.44223 | -0.38442 | -2.8406 | 19.0049
2020 | 277190.1498 | 110031.3696 | 167158.7802 | 20.4842 | 26.6899 | 2253903.1605 | 4461455.0569 | 6715358.2174 | 24.2265 | 0.48195 | -0.41895 | -2.8406 | 21.449
2021 | 277190.1414 | 99391.4508 | 177798.6906 | 20.0971 | 28.0859 | 1997477.649 | 4993631.222 | 6991108.871 | 25.2213 | 0.50579 | -0.43966 | -2.8406 | 22.4469
2022 | 277190.1899 | 91465.9252 | 185724.2647 | 21.7432 | 28.7178 | 1988765.4816 | 5333590.282 | 7322355.7636 | 26.4164 | 0.52376 | -0.45528 | -2.8406 | 23.6443
2023 | 277190.1852 | 89955.4879 | 187234.6974 | 24.0597 | 30.5159 | 2164299.6494 | 5713630.0481 | 7877929.6975 | 28.4207 | 0.55623 | -0.48351 | -2.8406 | 25.6528
2024 | 277190.1912 | 97672.1488 | 179518.0424 | 24.2877 | 32.2263 | 2372236.1639 | 5785210.921 | 8157447.0849 | 29.4291 | 0.58181 | -0.50575 | -2.8406 | 26.6646
2025 | 277190.1714 | 84713.8693 | 192476.3021 | 25.7769 | 33.7729 | 2183658.0376 | 6500487.5101 | 8684145.5477 | 31.3292 | 0.60972 | -0.53001 | -2.8406 | 28.5684
2026 | 277190.2399 | 88478.6533 | 188711.5866 | 26.7687 | 34.2732 | 2368456.8551 | 6467748.085 | 8836204.94 | 31.8778 | 0.62135 | -0.54012 | -2.8406 | 29.1184
2027 | 277190.257 | 79026.6382 | 198163.6188 | 26.4931 | 34.3519 | 2093657.1622 | 6807302.638 | 8900959.8002 | 32.1114 | 0.62137 | -0.54014 | -2.8406 | 29.3521
2028 | 277190.1967 | 67247.6803 | 209942.5164 | 28.6578 | 34.5236 | 1927173.7912 | 7247964.7894 | 9175138.5806 | 33.1005 | 0.62793 | -0.54584 | -2.8406 | 30.3421
2029 | 277190.1353 | 70534.0985 | 206656.0369 | 28.1192 | 35.0998 | 1983362.8042 | 7253590.8716 | 9236953.6758 | 33.3235 | 0.6348 | -0.55181 | -2.8406 | 30.566
2030 | 277190.1543 | 68589.6778 | 208600.4766 | 28.3175 | 35.7587 | 1942291.2528 | 7459283.8663 | 9401575.1191 | 33.9174 | 0.64556 | -0.56116 | -2.8406 | 31.1613
2031 | 277190.1494 | 60583.3973 | 216606.7521 | 28.2305 | 36.7249 | 1710301.3113 | 7954863.7414 | 9665165.0527 | 34.8684 | 0.66226 | -0.57568 | -2.8406 | 32.1144
2032 | 277190.1061 | 55350.5047 | 221839.6014 | 30.3419 | 38.4269 | 1679439.6326 | 8524610.0042 | 10204049.6369 | 36.8125 | 0.69217 | -0.60168 | -2.8406 | 34.0624
2033 | 277190.2191 | 60298.8049 | 216891.4142 | 30.2042 | 39.7943 | 1821275.8667 | 8631036.6856 | 10452312.5524 | 37.7081 | 0.7142 | -0.62083 | -2.8406 | 34.9609
2034 | 277190.1506 | 53248.1106 | 223942.04 | 30.3059 | 41.1449 | 1613732.3809 | 9214079.3231 | 10827811.704 | 39.0628 | 0.73653 | -0.64024 | -2.8406 | 36.3185
2035 | 277190.1062 | 55169.8834 | 222020.2228 | 31.8916 | 41.8944 | 1759455.4773 | 9301412.4439 | 11060867.9212 | 39.9035 | 0.75278 | -0.65437 | -2.8406 | 37.1614
2036 | 277190.2079 | 49696.5122 | 227493.6958 | 30.9348 | 42.3165 | 1537350.9551 | 9626734.1685 | 11164085.1236 | 40.2759 | 0.75886 | -0.65965 | -2.8406 | 37.5346

## Regulation Cost
Cost per MWh
2015 | 0.24 | EIA escalation
2016 | 0.28218 | 17.58%
2017 | 0.32163 | 13.98%
2018 | 0.35152 | 9.293%
2019 | 0.38442 | 9.36% | 2015 Integrated Marketplace Review: Regulation Support for Wind Integration (Feb 2, 2016)
2020 | 0.41895 | 8.982%
2021 | 0.43966 | 4.945%
2022 | 0.45528 | 3.552%
2023 | 0.48351 | 6.201%
2024 | 0.50575 | 4.598%
2025 | 0.53001 | 4.797%
2026 | 0.54012 | 1.908%
2027 | 0.54014 | 0.00289%
2028 | 0.54584 | 1.056%
2029 | 0.55181 | 1.094%
2030 | 0.56116 | 1.694%
2031 | 0.57568 | 2.586%
2032 | 0.60168 | 4.517%
2033 | 0.62083 | 3.184%
2034 | 0.64024 | 3.126%
2035 | 0.65437 | 2.206%
2036 | 0.65965 | 0.8074%
Average cost of regulation per MWhr of wind energy:
  Annual regulation cost for wind / Annual wind energy
  $7.6 million / 32.1 million MWhr
  = $0.24/MWhr

## Rev Req
NorthWestern Energy
Revenue Requirement - Regulated
Juhl Wind (Brule, Davison, Aurora)
Network Upgrades |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40
|  | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055
Rate Base:
Project Capitalize? (yes = capital, no = expense) | yes | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252 | 7291252
Less:
Accumulated Depreciation (Book Life) |  | 151611.2289 | 303222.4578 | 454833.6867 | 606444.9156 | 758056.1444 | 909667.3733 | 1061278.6022 | 1212889.8311 | 1364501.06 | 1516112.2889 | 1667723.5178 | 1819334.7467 | 1970945.9756 | 2122557.2044 | 2274168.4333 | 2425779.6622 | 2577390.8911 | 2729002.12 | 2880613.3489 | 3032224.5778 | 3183835.8067 | 3335447.0356 | 3487058.2644 | 3638669.4933 | 3790280.7222 | 3941891.9511 | 4093503.18 | 4245114.4089 | 4396725.6378 | 4548336.8667 | 4699948.0956 | 4851559.3244 | 5003170.5533 | 5154781.7822 | 5306393.0111 | 5458004.24 | 5609615.4689 | 5761226.6978 | 5912837.9267 | 6064449.1556
Deferred Income Taxes |  | 76202.89 | 268628.73 | 436305.18 | 581893.07 | 707514.01 | 815125.25 | 914246.85 | 1013171.61 | 1112157.24 | 1210885.59 | 1309871.22 | 1408599.57 | 1507585.2 | 1606313.55 | 1705299.18 | 1728131.39 | 1675067.46 | 1622003.53 | 1568939.6 | 1515875.67 | 1462811.74 | 1409747.81 | 1356683.88 | 1303619.95 | 1250556.02 | 1197492.09 | 1144428.16 | 1091364.23 | 1038300.3 | 985236.37 | 932172.44 | 879108.51 | 826044.58 | 772980.65 | 719916.72 | 666852.79 | 613788.86 | 560724.93 | 507661 | 454597.07
Total Year End Rate Base |  | 7063437.8811 | 6719400.8122 | 6400113.1333 | 6102914.0144 | 5825681.8456 | 5566459.3767 | 5315726.5478 | 5065190.5589 | 4814593.7 | 4564254.1211 | 4313657.2622 | 4063317.6833 | 3812720.8244 | 3562381.2456 | 3311784.3867 | 3137340.9478 | 3038793.6489 | 2940246.35 | 2841699.0511 | 2743151.7522 | 2644604.4533 | 2546057.1544 | 2447509.8556 | 2348962.5567 | 2250415.2578 | 2151867.9589 | 2053320.66 | 1954773.3611 | 1856226.0622 | 1757678.7633 | 1659131.4644 | 1560584.1656 | 1462036.8667 | 1363489.5678 | 1264942.2689 | 1166394.97 | 1067847.6711 | 969300.3722 | 870753.0733 | 772205.7744
Average Annual Rate Base |  | 7177344.94 | 6891419.3467 | 6559756.9728 | 6251513.5739 | 5964297.93 | 5696070.6111 | 5441092.9622 | 5190458.5533 | 4939892.1294 | 4689423.9106 | 4438955.6917 | 4188487.4728 | 3938019.2539 | 3687551.035 | 3437082.8161 | 3224562.6672 | 3088067.2983 | 2989519.9994 | 2890972.7006 | 2792425.4017 | 2693878.1028 | 2595330.8039 | 2496783.505 | 2398236.2061 | 2299688.9072 | 2201141.6083 | 2102594.3094 | 2004047.0106 | 1905499.7117 | 1806952.4128 | 1708405.1139 | 1609857.815 | 1511310.5161 | 1412763.2172 | 1314215.9183 | 1215668.6194 | 1117121.3206 | 1018574.0217 | 920026.7228 | 821479.4239
Return (Avg. Rate Base*Cost of Capital) | 7.24% | 519639.77 | 498938.76 | 474926.4 | 452609.58 | 431815.17 | 412395.51 | 393935.13 | 375789.2 | 357648.19 | 339514.29 | 321380.39 | 303246.49 | 285112.59 | 266978.69 | 248844.8 | 233458.34 | 223576.07 | 216441.25 | 209306.42 | 202171.6 | 195036.77 | 187901.95 | 180767.13 | 173632.3 | 166497.48 | 159362.65 | 152227.83 | 145093 | 137958.18 | 130823.35 | 123688.53 | 116553.71 | 109418.88 | 102284.06 | 95149.23 | 88014.41 | 80879.58 | 73744.76 | 66609.93 | 59475.11
Property Taxes | 0.7829% | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0% | 1 2016: 0; 2 2017: 0; 3 2018: 0; 4 2019: 0; 5 2020: 0; 6 2021: 0; 7 2022: 0; 8 2023: 0; 9 2024: 0; 10 2025: 0; 11 2026: 0; 12 2027: 0; 13 2028: 0; 14 2029: 0; 15 2030: 0; 16 2031: 0; 17 2032: 0; 18 2033: 0; 19 2034: 0; 20 2035: 0; 21 2036: 0
Depreciation |  | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289
Deferred Income Taxes @ 35% |  | 76202.89 | 192425.84 | 167676.45 | 145587.89 | 125620.94 | 107611.24 | 99121.6 | 98924.76 | 98985.63 | 98728.35 | 98985.63 | 98728.35 | 98985.63 | 98728.35 | 98985.63 | 22832.21 | -53063.93 | -53063.93 | -53063.93 | -53063.93 | -53063.93 | -53063.93 | -53063.93 | -53063.93 | -53063.93 | -53063.93 | -53063.93 | -53063.93 | -53063.93 | -53063.93 | -53063.93 | -53063.93 | -53063.93 | -53063.93 | -53063.93 | -53063.93 | -53063.93 | -53063.93 | -53063.93 | -53063.93
Income Taxes |  | 1 2016: 106212.1; 2 2017: -17277.77; 3 2018: -957.71; 4 2019: 13296.74; 5 2020: 25963.99; 6 2021: 37156.58; 7 2022: 39165.87; 8 2023: 32992.74; 9 2024: 26563.63; 10 2025: 20455.16; 11 2026: 13832.14; 12 2027: 7723.67; 13 2028: 1100.64; 14 2029: -5007.83; 15 2030: -11630.85; 16 2031: 59121.29; 17 2032: 131548.35; 18 2033: 129043.74; 19 2034: 126539.12; 20 2035: 124034.5; 21 2036: 121529.88
Total Revenue Requirement |  | 910749.1989 | 882781.2689 | 850339.5789 | 820188.6489 | 792094.5389 | 765857.7689 | 740917.0389 | 716401.1389 | 691891.8889 | 667392.2389 | 642892.5989 | 618392.9489 | 593893.2989 | 569393.6489 | 544894.0189 | 524106.2789 | 510754.9289 | 501115.4989 | 491476.0489 | 481836.6089 | 472197.1589 | 343532.4589 | 336397.6389 | 329262.8089 | 322127.9889 | 257909.9489 | 250775.1289 | 243640.2989 | 236505.4789 | 229370.6489 | 222235.8289 | 215101.0089 | 207966.1789 | 200831.3589 | 193696.5289 | 186561.7089 | 179426.8789 | 172292.0589 | 165157.2289 | 158022.4089
Income Taxes:
Revenues |  | 910749.1989 | 882781.2689 | 850339.5789 | 820188.6489 | 792094.5389 | 765857.7689 | 740917.0389 | 716401.1389 | 691891.8889 | 667392.2389 | 642892.5989 | 618392.9489 | 593893.2989 | 569393.6489 | 544894.0189 | 524106.2789 | 510754.9289 | 501115.4989 | 491476.0489 | 481836.6089 | 472197.1589 | 343532.4589 | 336397.6389 | 329262.8089 | 322127.9889 | 257909.9489 | 250775.1289 | 243640.2989 | 236505.4789 | 229370.6489 | 222235.8289 | 215101.0089 | 207966.1789 | 200831.3589 | 193696.5289 | 186561.7089 | 179426.8789 | 172292.0589 | 165157.2289 | 158022.4089
Property Taxes |  | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 57083.21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MACRS
yes
Tax Depreciation | 15 | 367535.8 | 698318.02 | 628486.22 | 566005.13 | 509404.62 | 457949.61 | 433692.24 | 433692.24 | 434427.32 | 433692.24 | 434427.32 | 433692.24 | 434427.32 | 433692.24 | 434427.32 | 216846.12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tax Depreciation | 7 | 1797.97 | 3081.33 | 2200.59 | 1571.49 | 1123.57 | 1122.31 | 1123.57 | 561.16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Interest Expense (Based on Avg. Rate Base) | 2.52% | 180869.09 | 173663.77 | 165305.88 | 157538.14 | 150300.31 | 143540.98 | 137115.54 | 130799.56 | 124485.28 | 118173.48 | 111861.68 | 105549.88 | 99238.09 | 92926.29 | 86614.49 | 81258.98 | 77819.3 | 75335.9 | 72852.51 | 70369.12 | 67885.73 | 65402.34 | 62918.94 | 60435.55 | 57952.16 | 55468.77 | 52985.38 | 50501.98 | 48018.59 | 45535.2 | 43051.81 | 40568.42 | 38085.03 | 35601.63 | 33118.24 | 30634.85 | 28151.46 | 25668.07 | 23184.67 | 20701.28
Federal Taxable Income |  | 303463.1289 | -49365.0611 | -2736.3211 | 37990.6789 | 74182.8289 | 106161.6589 | 111902.4789 | 94264.9689 | 75896.0789 | 58443.3089 | 39520.3889 | 22067.6189 | 3144.6789 | -14308.0911 | -33231.0011 | 168917.9689 | 375852.4189 | 368696.3889 | 361540.3289 | 354384.2789 | 347228.2189 | 221046.9089 | 216395.4889 | 211744.0489 | 207092.6189 | 202441.1789 | 197789.7489 | 193138.3189 | 188486.8889 | 183835.4489 | 179184.0189 | 174532.5889 | 169881.1489 | 165229.7289 | 160578.2889 | 155926.8589 | 151275.4189 | 146623.9889 | 141972.5589 | 137321.1289
Federal Income Tax @ 35% | 35% | 106212.1 | -17277.77 | -957.71 | 13296.74 | 25963.99 | 37156.58 | 39165.87 | 32992.74 | 26563.63 | 20455.16 | 13832.14 | 7723.67 | 1100.64 | -5007.83 | -11630.85 | 59121.29 | 131548.35 | 129043.74 | 126539.12 | 124034.5 | 121529.88 | 77366.42 | 75738.42 | 74110.42 | 72482.42 | 70854.41 | 69226.41 | 67598.41 | 65970.41 | 64342.41 | 62714.41 | 61086.41 | 59458.4 | 57830.41 | 56202.4 | 54574.4 | 52946.4 | 51318.4 | 49690.4 | 48062.4
Federal Taxable Income |  | 303463.1289 | -49365.0611 | -2736.3211 | 37990.6789 | 74182.8289 | 106161.6589 | 111902.4789 | 94264.9689 | 75896.0789 | 58443.3089 | 39520.3889 | 22067.6189 | 3144.6789 | -14308.0911 | -33231.0011 | 168917.9689 | 375852.4189 | 368696.3889 | 361540.3289 | 354384.2789 | 347228.2189 | 221046.9089 | 216395.4889 | 211744.0489 | 207092.6189 | 202441.1789 | 197789.7489 | 193138.3189 | 188486.8889 | 183835.4489 | 179184.0189 | 174532.5889 | 169881.1489 | 165229.7289 | 160578.2889 | 155926.8589 | 151275.4189 | 146623.9889 | 141972.5589 | 137321.1289
Juhl Wind Interconnection Costs (60MW)
20-year PMT of the NPV of Rev Req Cost |  | 1 2016: 787368.3807
Levelized Cost per MW |  | 1 2016: 2.8406
Brule County Facilities Study - Draft |  | 2 2017: Davison County Facilities Study - Draft; 8 2023: Aurora County Facilities Study - Draft
[15 empty] | 5225644 | Sub
[15 empty] | 434677 | Trans
[15 empty] | 1133499 | Relay
[15 empty] | 25341 | Comm
[15 empty] | 6727 | EMS
[15 empty] | 465364 | Land
7291252

## Depr
Book Depreciation
| Network Plant: |  | Basis | tax life | Book Life |  | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056
| Transmission |  | 434677 | 15 | 50 |  | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54 | 8693.54
| Metering |  | 0 | 15
| Lands & Permitting |  | 465364 | 0 | 0
| Substation/Relaying |  | 6359143 | 15 | 45 |  | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889 | 141314.2889
| EMS & Communications |  | 32068 | 7 | 20 |  | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4 | 1603.4
|  |  | 7291252 |  |  |  | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289 | 151611.2289
Tax Depreciation |  | MACRS
Tax Depreciation - Yrs |  | 15
| Annual | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
Vintage Yr | Expenditure | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046
2017 | 6793820 | 339691 | 645412.9 | 580871.61 | 523124.14 | 470811.73 | 423254.99 | 400835.38 | 400835.38 | 401514.76 | 400835.38 | 401514.76 | 400835.38 | 401514.76 | 400835.38 | 401514.76 | 200417.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026 | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2028 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2029 | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2030 | 0 | 2030: 0; 2031: 0; 2032: 0; 2033: 0; 2034: 0; 2035: 0; 2036: 0; 2037: 0; 2038: 0; 2039: 0; 2040: 0; 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0
2031 | 0 | 2031: 0; 2032: 0; 2033: 0; 2034: 0; 2035: 0; 2036: 0; 2037: 0; 2038: 0; 2039: 0; 2040: 0; 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0
2032 | 0 | 2032: 0; 2033: 0; 2034: 0; 2035: 0; 2036: 0; 2037: 0; 2038: 0; 2039: 0; 2040: 0; 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0
2033 | 0 | 2033: 0; 2034: 0; 2035: 0; 2036: 0; 2037: 0; 2038: 0; 2039: 0; 2040: 0; 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0
2034 | 0 | 2034: 0; 2035: 0; 2036: 0; 2037: 0; 2038: 0; 2039: 0; 2040: 0; 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0
2035 | 0 | 2035: 0; 2036: 0; 2037: 0; 2038: 0; 2039: 0; 2040: 0; 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0
2036 | 0 | 2036: 0; 2037: 0; 2038: 0; 2039: 0; 2040: 0; 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0
2037 | 0 | 2037: 0; 2038: 0; 2039: 0; 2040: 0; 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0
2038 | 0 | 2038: 0; 2039: 0; 2040: 0; 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0
2039 | 0 | 2039: 0; 2040: 0; 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0
2040 | 0 | 2040: 0; 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0
2041 | 0 | 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0
2042 | 0 | 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0
2043 | 0 | 2043: 0; 2044: 0; 2045: 0; 2046: 0
2044 | 0 | 2044: 0; 2045: 0; 2046: 0
2045 | 0 | 2045: 0; 2046: 0
2046 | 0 | 2046: 0
Total | 6793820 | 339691 | 645412.9 | 580871.61 | 523124.14 | 470811.73 | 423254.99 | 400835.38 | 400835.38 | 401514.76 | 400835.38 | 401514.76 | 400835.38 | 401514.76 | 400835.38 | 401514.76 | 200417.69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tax Depreciation |  | 2017: MACRS
Tax Depreciation - Yrs |  | 2017: 7
| Annual | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
Vintage Yr | Expenditure | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046
2017 | 32068 | 4582.52 | 7853.45 | 5608.69 | 4005.29 | 2863.67 | 2860.47 | 2863.67 | 1430.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2018 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2019 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2020 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2021 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2022 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2023 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2024 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2025 | 0 | [8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2026 | 0 | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2027 | 0 | [10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2028 | 0 | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2029 | 0 | [12 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2030 | 0 | 2030: 0; 2031: 0; 2032: 0; 2033: 0; 2034: 0; 2035: 0; 2036: 0; 2037: 0; 2038: 0; 2039: 0; 2040: 0; 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0
2031 | 0 | 2031: 0; 2032: 0; 2033: 0; 2034: 0; 2035: 0; 2036: 0; 2037: 0; 2038: 0; 2039: 0; 2040: 0; 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0
2032 | 0 | 2032: 0; 2033: 0; 2034: 0; 2035: 0; 2036: 0; 2037: 0; 2038: 0; 2039: 0; 2040: 0; 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0
2033 | 0 | 2033: 0; 2034: 0; 2035: 0; 2036: 0; 2037: 0; 2038: 0; 2039: 0; 2040: 0; 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0
2034 | 0 | 2034: 0; 2035: 0; 2036: 0; 2037: 0; 2038: 0; 2039: 0; 2040: 0; 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0
2035 | 0 | 2035: 0; 2036: 0; 2037: 0; 2038: 0; 2039: 0; 2040: 0; 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0
2036 | 0 | 2036: 0; 2037: 0; 2038: 0; 2039: 0; 2040: 0; 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0
2037 | 0 | 2037: 0; 2038: 0; 2039: 0; 2040: 0; 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0
2038 | 0 | 2038: 0; 2039: 0; 2040: 0; 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0
2039 | 0 | 2039: 0; 2040: 0; 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0
2040 | 0 | 2040: 0; 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0
2041 | 0 | 2041: 0; 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0
2042 | 0 | 2042: 0; 2043: 0; 2044: 0; 2045: 0; 2046: 0
2043 | 0 | 2043: 0; 2044: 0; 2045: 0; 2046: 0
2044 | 0 | 2044: 0; 2045: 0; 2046: 0
2045 | 0 | 2045: 0; 2046: 0
2046 | 0 | 2046: 0
Total | 32068 | 4582.52 | 7853.45 | 5608.69 | 4005.29 | 2863.67 | 2860.47 | 2863.67 | 1430.23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## EIA AEO
Electric Power Projections by Electricity Market Module Region
http://www.eia.gov/forecasts/aeo/data/browser/#/?id=62-AEO2016&region=3-17&cases=ref_no_cpp&start=2013&end=2040&f=A&linechart=ref_no_cpp-d032316a.5-62-AEO2016.3-17&sourcekey=0
Tue Oct 11 2016 11:20:40 GMT-0600 (Mountain Daylight Time)
Source: U.S. Energy Information Administration
Southwest Power Pool / North | full name | api key | units | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | Growth (2015-2040)
Net Summer Electricity Generating Capacity |  | 62-AEO2016.2.
(gigawatts) |  | 62-AEO2016.3.
Electric Power Sector |  | 62-AEO2016.4.
Coal | Electricity: Electric Power Sector: Capacity: Coal: Reference case without Clean Power Plan | 62-AEO2016.5.ref_no_cpp-d032316a | GW | 8.5087 | 8.4402 | 7.574 | 7.574 | 7.574 | 7.574 | 7.4771 | 7.4771 | 7.1371 | 7.5012 | 7.5012 | 7.5012 | 7.5012 | 7.5012 | 7.5012 | 7.5012 | 7.5012 | 7.5012 | 7.5012 | 7.5012 | 7.5012 | 7.5012 | 7.5012 | 7.5012 | 7.5012 | 7.5012 | 7.5012 | -0.5%
Oil and Natural Gas Steam 3 |  | Electricity: Electric Power Sector: Capacity: Oil and Natural Gas Steam: Reference case without Clean Power Plan | 62-AEO2016.6.ref_no_cpp-d032316a | GW | 1.7544 | 1.6694 | 1.7657 | 1.7657 | 1.7657 | 1.7657 | 1.736 | 1.3458 | 0.8428 | 0.524 | 0.524 | 0.524 | 0.524 | 0.524 | 0.524 | 0.524 | 0.524 | 0.524 | 0.524 | 0.524 | 0.524 | 0.524 | 0.524 | 0.524 | 0.524 | 0.524 | 0.524 | - -
Combined Cycle | Electricity: Electric Power Sector: Capacity: Combined Cycle: Reference case without Clean Power Plan | 62-AEO2016.7.ref_no_cpp-d032316a | GW | 1.3382 | 1.3382 | 1.4762 | 1.4762 | 1.4762 | 1.4762 | 1.4762 | 1.4762 | 1.4762 | 1.4762 | 1.4762 | 1.4762 | 1.4762 | 1.4762 | 1.4762 | 1.4762 | 1.4762 | 1.4762 | 1.4762 | 1.4762 | 1.4762 | 1.5196 | 1.5196 | 1.5196 | 1.5196 | 1.5196 | 1.5196 | 0.5%
Combustion Turbine/Diesel | Electricity: Electric Power Sector: Capacity: Combustion Turbine/Diesel: Reference case without Clean Power Plan | 62-AEO2016.8.ref_no_cpp-d032316a | GW | 5.3216 | 5.3016 | 5.3292 | 5.3853 | 5.5832 | 5.2652 | 4.9043 | 4.9043 | 4.9043 | 4.9043 | 4.9043 | 4.9986 | 5.0622 | 5.1305 | 5.2356 | 5.3524 | 5.4842 | 5.6488 | 5.6879 | 5.801 | 5.9154 | 5.9432 | 6.047 | 6.2101 | 6.3375 | 6.5061 | 6.6323 | 0.9%
Nuclear Power | Electricity: Electric Power Sector: Capacity: Nuclear: Reference case without Clean Power Plan | 62-AEO2016.9.ref_no_cpp-d032316a | GW | 1.175 | 1.175 | 1.175 | 1.175 | 1.175 | 1.175 | 1.175 | 1.175 | 1.175 | 1.175 | 1.175 | 1.175 | 1.175 | 1.175 | 1.175 | 1.175 | 1.175 | 1.175 | 1.175 | 1.175 | 1.175 | 1.175 | 1.175 | 1.175 | 1.175 | 1.175 | 1.175 | 0%
Pumped Storage | Electricity: Electric Power Sector: Capacity: Pumped Storage: Reference case without Clean Power Plan | 62-AEO2016.10.ref_no_cpp-d032316a | GW | [27 empty] | - -
Fuel Cells | Electricity: Electric Power Sector: Capacity: Fuel Cells: Reference case without Clean Power Plan | 62-AEO2016.11.ref_no_cpp-d032316a | GW | [27 empty] | - -
Renewable Sources | Electricity: Electric Power Sector: Capacity: Renewable Sources: Reference case without Clean Power Plan | 62-AEO2016.12.ref_no_cpp-d032316a | GW | 3.0025 | 3.9814 | 4.4352 | 4.4352 | 5.2073 | 6.3049 | 7.2629 | 7.8676 | 7.8676 | 7.8676 | 7.8676 | 7.9111 | 7.9633 | 8.0168 | 8.0699 | 8.1295 | 8.1946 | 8.1946 | 8.2279 | 8.2707 | 8.3317 | 8.3317 | 8.3662 | 8.3662 | 8.405 | 8.405 | 8.4418 | 3.1%
Distributed Generation | Electricity: Electric Power Sector: Capacity: Distributed Generation: Reference case without Clean Power Plan | 62-AEO2016.13.ref_no_cpp-d032316a | GW | [27 empty] | - -
Total Capacity | Electricity: Electric Power Sector: Capacity: Total Capacity: Reference case without Clean Power Plan | 62-AEO2016.14.ref_no_cpp-d032316a | GW | 21.1004 | 21.9058 | 21.7553 | 21.8114 | 22.7814 | 23.561 | 24.0314 | 24.246 | 23.403 | 23.4483 | 22.9243 | 23.062 | 23.1778 | 23.2997 | 23.4579 | 23.6343 | 23.8312 | 23.9958 | 24.0682 | 24.2241 | 24.3996 | 24.4707 | 24.6091 | 24.7721 | 24.9384 | 25.107 | 25.27 | 0.6%
Cumulative Planned Additions |  | 62-AEO2016.16.
Coal | Electricity: Electric Power Sector: Cumulative Planned Additions: Coal: Reference case without Clean Power Plan | 62-AEO2016.17.ref_no_cpp-d032316a | GW | - - | - - | [25 empty] | - -
Oil and Natural Gas Steam | Electricity: Electric Power Sector: Cumulative Planned Additions: Oil and Natural Gas Steam: Reference case without Clean Power Plan | 62-AEO2016.18.ref_no_cpp-d032316a | GW | - - | - - | [25 empty] | - -
Combined Cycle | Electricity: Electric Power Sector: Cumulative Planned Additions: Combined Cycle: Reference case without Clean Power Plan | 62-AEO2016.19.ref_no_cpp-d032316a | GW | - - | - - | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | 0.138 | - -
Combustion Turbine/Diesel | Electricity: Electric Power Sector: Cumulative Planned Additions: Combustion Turbine/Diesel: Reference case without Clean Power Plan | 62-AEO2016.20.ref_no_cpp-d032316a | GW | - - | - - | 0.0276 | 0.0837 | 0.0837 | 0.0837 | 0.0837 | 0.0837 | 0.0837 | 0.0837 | 0.0837 | 0.0837 | 0.0837 | 0.0837 | 0.0837 | 0.0837 | 0.0837 | 0.0837 | 0.0837 | 0.0837 | 0.0837 | 0.0837 | 0.0837 | 0.0837 | 0.0837 | 0.0837 | 0.0837 | - -
Nuclear Power | Electricity: Electric Power Sector: Cumulative Planned Additions: Nuclear: Reference case without Clean Power Plan | 62-AEO2016.21.ref_no_cpp-d032316a | GW | - - | - - | [25 empty] | - -
Pumped Storage | Electricity: Electric Power Sector: Cumulative Planned Additions: Pumped Storage: Reference case without Clean Power Plan | 62-AEO2016.22.ref_no_cpp-d032316a | GW | - - | - - | [25 empty] | - -
Fuel Cells | Electricity: Electric Power Sector: Cumulative Planned Additions: Fuel Cells: Reference case without Clean Power Plan | 62-AEO2016.23.ref_no_cpp-d032316a | GW | - - | - - | [25 empty] | - -
Renewable Sources | Electricity: Electric Power Sector: Cumulative Planned Additions: Renewable Sources: Reference case without Clean Power Plan | 62-AEO2016.24.ref_no_cpp-d032316a | GW | - - | - - | 0.4538 | 0.4538 | 0.4538 | 0.4538 | 0.4538 | 0.4538 | 0.4538 | 0.4538 | 0.4538 | 0.4538 | 0.4538 | 0.4538 | 0.4538 | 0.4538 | 0.4538 | 0.4538 | 0.4538 | 0.4538 | 0.4538 | 0.4538 | 0.4538 | 0.4538 | 0.4538 | 0.4538 | 0.4538 | - -
Distributed Generation | Electricity: Electric Power Sector: Cumulative Planned Additions: Distributed Generation: Reference case without Clean Power Plan | 62-AEO2016.25.ref_no_cpp-d032316a | GW | - - | - - | [25 empty] | - -
Total Planned Additions | Electricity: Electric Power Sector: Cumulative Planned Additions: Total Planned Additions: Reference case without Clean Power Plan | 62-AEO2016.26.ref_no_cpp-d032316a | GW | - - | - - | 0.6194 | 0.6755 | 0.6755 | 0.6755 | 0.6755 | 0.6755 | 0.6755 | 0.6755 | 0.6755 | 0.6755 | 0.6755 | 0.6755 | 0.6755 | 0.6755 | 0.6755 | 0.6755 | 0.6755 | 0.6755 | 0.6755 | 0.6755 | 0.6755 | 0.6755 | 0.6755 | 0.6755 | 0.6755 | - -
Cumulative Unplanned Additions |  | 62-AEO2016.27.
Coal | Electricity: Electric Power Sector: Cumulative Unplanned Additions: Coal: Reference case without Clean Power Plan | 62-AEO2016.28.ref_no_cpp-d032316a | GW | - - | - - | [25 empty] | - -
Oil and Natural Gas Steam | Electricity: Electric Power Sector: Cumulative Unplanned Additions: Oil and Natural Gas Steam: Reference case without Clean Power Plan | 62-AEO2016.29.ref_no_cpp-d032316a | GW | - - | - - | [25 empty] | - -
Combined Cycle | Electricity: Electric Power Sector: Cumulative Unplanned Additions: Combined Cycle: Reference case without Clean Power Plan | 62-AEO2016.30.ref_no_cpp-d032316a | GW | - - | - - | [19 empty] | 0.043436 | 0.043436 | 0.043436 | 0.043436 | 0.043436 | 0.043436 | - -
Combustion Turbine/Diesel | Electricity: Electric Power Sector: Cumulative Unplanned Additions: Combustion Turbine/Diesel: Reference case without Clean Power Plan | 62-AEO2016.31.ref_no_cpp-d032316a | GW | - - | - - |  |  | 0.19788 | 0.19788 | 0.19788 | 0.19788 | 0.19788 | 0.19788 | 0.19788 | 0.29368 | 0.35839 | 0.42671 | 0.53178 | 0.64864 | 0.78041 | 0.94497 | 0.98405 | 1.0972 | 1.2116 | 1.3132 | 1.417 | 1.5801 | 1.7075 | 1.8761 | 2.0023 | - -
Nuclear Power | Electricity: Electric Power Sector: Cumulative Unplanned Additions: Nuclear: Reference case without Clean Power Plan | 62-AEO2016.32.ref_no_cpp-d032316a | GW | - - | - - | [25 empty] | - -
Pumped Storage | Electricity: Electric Power Sector: Cumulative Unplanned Additions: Pumped Storage: Reference case without Clean Power Plan | 62-AEO2016.33.ref_no_cpp-d032316a | GW | - - | - - | [25 empty] | - -
Fuel Cells | Electricity: Electric Power Sector: Cumulative Unplanned Additions: Fuel Cells: Reference case without Clean Power Plan | 62-AEO2016.34.ref_no_cpp-d032316a | GW | - - | - - | [25 empty] | - -
Renewable Sources | Electricity: Electric Power Sector: Cumulative Unplanned Additions: Renewable Sources: Reference case without Clean Power Plan | 62-AEO2016.35.ref_no_cpp-d032316a | GW | - - | - - |  |  | 0.77212 | 1.8697 | 2.8277 | 3.4324 | 3.4324 | 3.4324 | 3.4324 | 3.4759 | 3.5281 | 3.5816 | 3.6347 | 3.6943 | 3.7594 | 3.7594 | 3.7927 | 3.8355 | 3.8965 | 3.8965 | 3.931 | 3.931 | 3.9698 | 3.9698 | 4.0066 | - -
Distributed Generation | Electricity: Electric Power Sector: Cumulative Unplanned Additions: Distributed Generation: Reference case without Clean Power Plan | 62-AEO2016.36.ref_no_cpp-d032316a | GW | - - | - - | [25 empty] | - -
Total Unplanned Additions | Electricity: Electric Power Sector: Cumulative Unplanned Additions: Total Unplanned Additions: Reference case without Clean Power Plan | 62-AEO2016.37.ref_no_cpp-d032316a | GW | - - | - - |  |  | 0.97 | 2.0676 | 3.0255 | 3.6303 | 3.6303 | 3.6303 | 3.6303 | 3.7695 | 3.8864 | 4.0083 | 4.1665 | 4.3429 | 4.5398 | 4.7044 | 4.7768 | 4.9327 | 5.1082 | 5.2531 | 5.3914 | 5.5545 | 5.7208 | 5.8894 | 6.0524 | - -
Cumulative Electric Power Sector Additions | Electricity: Electric Power Sector: Cumulative Total Additions: Reference case without Clean Power Plan | 62-AEO2016.38.ref_no_cpp-d032316a | GW | - - | - - | 0.6194 | 0.6755 | 1.6455 | 2.7431 | 3.701 | 4.3058 | 4.3058 | 4.3058 | 4.3058 | 4.445 | 4.5619 | 4.6838 | 4.842 | 5.0184 | 5.2153 | 5.3799 | 5.4523 | 5.6082 | 5.7836 | 5.9286 | 6.0669 | 6.23 | 6.3963 | 6.5649 | 6.7279 | - -
Cumulative Retirements |  | 62-AEO2016.40.
Coal | Electricity: Electric Power Sector: Cumulative Retirements: Coal: Reference case without Clean Power Plan | 62-AEO2016.41.ref_no_cpp-d032316a | GW | - - | - - | 0.4058 | 0.4058 | 0.4058 | 0.4058 | 0.5027 | 0.5027 | 0.8427 | 0.8427 | 0.8427 | 0.8427 | 0.8427 | 0.8427 | 0.8427 | 0.8427 | 0.8427 | 0.8427 | 0.8427 | 0.8427 | 0.8427 | 0.8427 | 0.8427 | 0.8427 | 0.8427 | 0.8427 | 0.8427 | - -
Oil and Natural Gas Steam | Electricity: Electric Power Sector: Cumulative Retirements: Oil and Natural Gas Steam: Reference case without Clean Power Plan | 62-AEO2016.42.ref_no_cpp-d032316a | GW | - - | - - |  |  |  |  | 0.0297 | 0.4199 | 0.9229 | 1.2417 | 1.7657 | 1.7657 | 1.7657 | 1.7657 | 1.7657 | 1.7657 | 1.7657 | 1.7657 | 1.7657 | 1.7657 | 1.7657 | 1.7657 | 1.7657 | 1.7657 | 1.7657 | 1.7657 | 1.7657 | - -
Combined Cycle | Electricity: Electric Power Sector: Cumulative Retirements: Combined Cycle: Reference case without Clean Power Plan | 62-AEO2016.43.ref_no_cpp-d032316a | GW | - - | - - | [25 empty] | - -
Combustion Turbine/Diesel | Electricity: Electric Power Sector: Cumulative Retirements: Combustion Turbine/Diesel: Reference case without Clean Power Plan | 62-AEO2016.44.ref_no_cpp-d032316a | GW | - - | - - |  |  |  | 0.318 | 0.6789 | 0.6789 | 0.6789 | 0.6789 | 0.6789 | 0.6804 | 0.6815 | 0.6815 | 0.6815 | 0.6815 | 0.6815 | 0.6815 | 0.6815 | 0.6815 | 0.6815 | 0.7553 | 0.7553 | 0.7553 | 0.7553 | 0.7553 | 0.7553 | - -
Nuclear Power | Electricity: Electric Power Sector: Cumulative Retirements: Nuclear: Reference case without Clean Power Plan | 62-AEO2016.45.ref_no_cpp-d032316a | GW | - - | - - | [25 empty] | - -
Pumped Storage | Electricity: Electric Power Sector: Cumulative Retirements: Pumped Storage: Reference case without Clean Power Plan | 62-AEO2016.46.ref_no_cpp-d032316a | GW | - - | - - | [25 empty] | - -
Fuel Cells | Electricity: Electric Power Sector: Cumulative Retirements: Fuel Cells: Reference case without Clean Power Plan | 62-AEO2016.47.ref_no_cpp-d032316a | GW | - - | - - | [25 empty] | - -
Renewable Sources | Electricity: Electric Power Sector: Cumulative Retirements: Renewable Sources: Reference case without Clean Power Plan | 62-AEO2016.48.ref_no_cpp-d032316a | GW | - - | - - | [25 empty] | - -
Total | Electricity: Electric Power Sector: Cumulative Retirements: Total: Reference case without Clean Power Plan | 62-AEO2016.49.ref_no_cpp-d032316a | GW | - - | - - | 0.4058 | 0.4058 | 0.4058 | 0.7238 | 1.2113 | 1.6015 | 2.4445 | 2.7633 | 3.2873 | 3.2888 | 3.2899 | 3.2899 | 3.2899 | 3.2899 | 3.2899 | 3.2899 | 3.2899 | 3.2899 | 3.2899 | 3.3637 | 3.3637 | 3.3637 | 3.3637 | 3.3637 | 3.3637 | - -
End-Use Sectors |  | 62-AEO2016.52.
Coal | Electricity: End-Use Sectors: Capacity: Coal: Reference case without Clean Power Plan | 62-AEO2016.53.ref_no_cpp-d032316a | GW | [27 empty] | - -
Petroleum | Electricity: End-Use Sectors: Capacity: Petroleum: Reference case without Clean Power Plan | 62-AEO2016.54.ref_no_cpp-d032316a | GW | [27 empty] | - -
Natural Gas | Electricity: End-Use Sectors: Capacity: Natural Gas: Reference case without Clean Power Plan | 62-AEO2016.55.ref_no_cpp-d032316a | GW | 0.030283 | 0.032183 | 0.034417 | 0.036061 | 0.037256 | 0.0388 | 0.040375 | 0.042141 | 0.044074 | 0.046193 | 0.048521 | 0.051133 | 0.054134 | 0.057464 | 0.061038 | 0.064962 | 0.069363 | 0.073944 | 0.078688 | 0.083625 | 0.088842 | 0.094377 | 0.098666 | 0.10207 | 0.10489 | 0.10746 | 0.11007 | 5%
Other Gaseous Fuels | Electricity: End-Use Sectors: Capacity: Other Gaseous Fuels: Reference case without Clean Power Plan | 62-AEO2016.56.ref_no_cpp-d032316a | GW | [27 empty] | - -
Renewable Sources | Electricity: End-Use Sectors: Capacity: Renewable Sources: Reference case without Clean Power Plan | 62-AEO2016.57.ref_no_cpp-d032316a | GW | 0.004058 | 0.010329 | 0.017931 | 0.025716 | 0.034615 | 0.044218 | 0.05406 | 0.06411 | 0.06849 | 0.069632 | 0.071146 | 0.073247 | 0.075739 | 0.07867 | 0.08195 | 0.085511 | 0.089425 | 0.093543 | 0.097823 | 0.10215 | 0.10653 | 0.11103 | 0.11549 | 0.11995 | 0.12446 | 0.12898 | 0.13354 | 10.8%
Other | Electricity: End-Use Sectors: Capacity: Other: Reference case without Clean Power Plan | 62-AEO2016.58.ref_no_cpp-d032316a | GW | [27 empty] | - -
Total | Electricity: End-Use Sectors: Capacity: Total: Reference case without Clean Power Plan | 62-AEO2016.59.ref_no_cpp-d032316a | GW | 0.034342 | 0.042512 | 0.052348 | 0.061777 | 0.071871 | 0.083017 | 0.094435 | 0.10625 | 0.11256 | 0.11582 | 0.11967 | 0.12438 | 0.12987 | 0.13613 | 0.14299 | 0.15047 | 0.15879 | 0.16749 | 0.17651 | 0.18577 | 0.19537 | 0.20541 | 0.21415 | 0.22202 | 0.22934 | 0.23644 | 0.24361 | 7.2%
Electricity Sales |  | 62-AEO2016.61.
(billion kilowatthours) |  | 62-AEO2016.62.
Residential | Electricity: Electricity Demand: Residential: Reference case without Clean Power Plan | 62-AEO2016.63.ref_no_cpp-d032316a | BkWh | 22.6807 | 21.4957 | 22.6448 | 22.5675 | 22.5734 | 22.5263 | 22.2354 | 22.1409 | 22.1926 | 22.3024 | 22.4398 | 22.5516 | 22.6758 | 22.8108 | 22.9534 | 23.1049 | 23.2057 | 23.2998 | 23.3994 | 23.5251 | 23.6782 | 23.8524 | 24.0194 | 24.182 | 24.3413 | 24.508 | 24.6879 | 0.6%
Commercial/Other | Electricity: Electricity Demand: Commercial/Other: Reference case without Clean Power Plan | 62-AEO2016.64.ref_no_cpp-d032316a | BkWh | 25.5337 | 25.9427 | 25.7604 | 25.5596 | 25.3795 | 25.5709 | 25.7343 | 25.9487 | 26.2138 | 26.5035 | 26.8026 | 27.1018 | 27.402 | 27.6963 | 27.9971 | 28.303 | 28.5582 | 28.8045 | 29.0598 | 29.3404 | 29.6368 | 29.9382 | 30.2342 | 30.5337 | 30.8283 | 31.1242 | 31.4185 | 0.8%
Industrial | Electricity: Electricity Demand: Industrial: Reference case without Clean Power Plan | 62-AEO2016.65.ref_no_cpp-d032316a | BkWh | 15.475 | 14.9656 | 15.0922 | 15.1004 | 14.8819 | 15.2992 | 15.6182 | 15.9272 | 16.1879 | 16.4968 | 16.7193 | 16.9143 | 17.0732 | 17.2002 | 17.2028 | 17.2423 | 17.27 | 17.2722 | 17.2903 | 17.3297 | 17.3639 | 17.3948 | 17.4621 | 17.5332 | 17.6437 | 17.706 | 17.7887 | 0.7%
Transportation | Electricity: Electricity Demand: Transportation: Reference case without Clean Power Plan | 62-AEO2016.66.ref_no_cpp-d032316a | BkWh | 0.027079 | 0.041395 | 0.052236 | 0.063576 | 0.07184 | 0.083738 | 0.099283 | 0.11961 | 0.14391 | 0.17011 | 0.19837 | 0.22776 | 0.25482 | 0.28051 | 0.30526 | 0.32975 | 0.35365 | 0.37644 | 0.39787 | 0.41805 | 0.43686 | 0.4538 | 0.46942 | 0.48364 | 0.49624 | 0.50779 | 0.51851 | 10.6%
Total Sales | Electricity: Electricity Demand: Total Sales: Reference case without Clean Power Plan | 62-AEO2016.67.ref_no_cpp-d032316a | BkWh | 63.7165 | 62.4454 | 63.5496 | 63.291 | 62.9066 | 63.4803 | 63.6872 | 64.1365 | 64.7382 | 65.4729 | 66.16 | 66.7954 | 67.4059 | 67.9878 | 68.4586 | 68.98 | 69.3875 | 69.7529 | 70.1474 | 70.6133 | 71.1157 | 71.6391 | 72.1852 | 72.7325 | 73.3095 | 73.846 | 74.4137 | 0.7%
Net Energy for Load (billion kilowatthours) |  | 62-AEO2016.69.
Gross International Imports | Electricity: Net Energy for Load: Gross International Imports: Reference case without Clean Power Plan | 62-AEO2016.70.ref_no_cpp-d032316a | BkWh | [27 empty] | - -
Gross International Exports | Electricity: Net Energy for Load: Gross International Exports: Reference case without Clean Power Plan | 62-AEO2016.71.ref_no_cpp-d032316a | BkWh | [27 empty] | - -
Gross Interregional Electricity Imports | Electricity: Net Energy for Load: Gross Interregional Electricity Imports: Reference case without Clean Power Plan | 62-AEO2016.72.ref_no_cpp-d032316a | BkWh | 4.3741 | 4.4372 | 5.1759 | 2.5176 | 2.3546 | 4.2663 | 4.9587 | 4.1572 | 5.1739 | 4.6865 | 3.7557 | 3.8936 | 3.1481 | 2.9009 | 3.2519 | 3.6504 | 2.9934 | 2.6927 | 2.9363 | 2.4152 | 2.5759 | 2.7694 | 2.6875 | 2.8573 | 1.3275 | 1.0588 | 1.3347 | -4.7%
Gross Interregional Electricity Exports | Electricity: Net Energy for Load: Gross Interregional Electricity Exports: Reference case without Clean Power Plan | 62-AEO2016.73.ref_no_cpp-d032316a | BkWh | 3.8189 | 1.6813 | 3.3436 | 6.0999 | 8.0094 | 16.6641 | 21.2398 | 22.7194 | 21.6557 | 23.0807 | 21.8297 | 21.8854 | 20.7371 | 20.2159 | 20.076 | 20.1889 | 18.7717 | 18.1531 | 18.004 | 17.8786 | 18.0647 | 17.7613 | 17.2819 | 16.8256 | 14.8087 | 13.9004 | 13.6854 | 8.7%
Purchases from Combined Heat and Power | Electricity: Net Energy for Load: Purchases from Combined Heat and Power: Reference case without Clean Power Plan | 62-AEO2016.74.ref_no_cpp-d032316a | BkWh | 0.058378 | 0.062395 | 0.066609 | 0.070044 | 0.070384 | 0.074072 | 0.078036 | 0.08251 | 0.086714 | 0.090649 | 0.094931 | 0.099676 | 0.10486 | 0.1104 | 0.11609 | 0.12208 | 0.12865 | 0.13543 | 0.14216 | 0.14918 | 0.15661 | 0.16471 | 0.17222 | 0.17941 | 0.18652 | 0.19427 | 0.20328 | 4.8%
Electric Power Sector Generation for Customer | Electricity: Net Energy for Load: Electric Power Sector Generation for Custome: Reference case without Clean Power Plan | 62-AEO2016.75.ref_no_cpp-d032316a | BkWh | 71.1824 | 65.0125 | 66.9824 | 72.179 | 73.7234 | 81.0278 | 85.0751 | 87.7806 | 86.2891 | 88.9904 | 89.4077 | 90.0062 | 90.2576 | 90.6061 | 90.6178 | 90.889 | 90.5621 | 90.6319 | 90.6582 | 91.5498 | 92.1101 | 92.17 | 92.3545 | 92.3119 | 92.4405 | 92.372 | 92.4852 | 1.4%
Total Net Energy for Load | Electricity: Net Energy for Load: Total Net Energy for Load: Reference case without Clean Power Plan | 62-AEO2016.76.ref_no_cpp-d032316a | BkWh | 71.7959 | 67.8307 | 68.8813 | 68.6668 | 68.139 | 68.7041 | 68.872 | 69.3009 | 69.894 | 70.6868 | 71.4286 | 72.1142 | 72.7734 | 73.4015 | 73.9098 | 74.4726 | 74.9124 | 75.307 | 75.7326 | 76.2356 | 76.7779 | 77.3428 | 77.9323 | 78.523 | 79.1458 | 79.7247 | 80.3378 | 0.7%
Generation by Fuel Type |  | 62-AEO2016.78.
(billion kilowatthours) |  | 62-AEO2016.79.
Electric Power Sector |  | 62-AEO2016.80.
Coal | Electricity: Electric Power Sector: Generation: Coal: Reference case without Clean Power Plan | 62-AEO2016.81.ref_no_cpp-d032316a | BkWh | 46.9607 | 41.4884 | 41.4546 | 46.0422 | 45.0881 | 47.423 | 47.5079 | 47.3381 | 45.1388 | 47.8501 | 48.073 | 48.4076 | 48.4055 | 48.1668 | 48.0095 | 48.0007 | 47.4337 | 47.42 | 47.4078 | 47.5998 | 47.5875 | 47.5757 | 47.561 | 47.5467 | 47.5354 | 47.5218 | 47.5099 | 0.5%
Petroleum | Electricity: Electric Power Sector: Generation: Petroleum: Reference case without Clean Power Plan | 62-AEO2016.82.ref_no_cpp-d032316a | BkWh | 0.113 | 0.16664 | 0.16663 | 0.18554 | 0.18171 | 0.19104 | 0.19132 | 0.19063 | 0.18293 | 0.19381 | 0.19475 | 0.19609 | 0.19608 | 0.19512 | 0.19449 | 0.19446 | 0.19218 | 0.19212 | 0.19208 | 0.19284 | 0.19281 | 0.19275 | 0.19269 | 0.19263 | 0.19259 | 0.19253 | 0.19248 | 0.6%
Natural Gas | Electricity: Electric Power Sector: Generation: Natural Gas: Reference case without Clean Power Plan | 62-AEO2016.83.ref_no_cpp-d032316a | BkWh | 4.5297 | 3.5353 | 3.2547 | 2.6922 | 2.5692 | 3.2323 | 3.3798 | 3.6041 | 3.833 | 3.8098 | 3.9944 | 4.117 | 4.1797 | 4.5395 | 4.4928 | 4.5358 | 4.5207 | 4.567 | 4.4983 | 5.0337 | 5.3681 | 5.3892 | 5.4774 | 5.4214 | 5.4154 | 5.329 | 5.3358 | 1.7%
Nuclear | Electricity: Electric Power Sector: Generation: Nuclear: Reference case without Clean Power Plan | 62-AEO2016.84.ref_no_cpp-d032316a | BkWh | 8.558 | 8.6953 | 8.4542 | 8.5376 | 8.5533 | 8.569 | 8.569 | 8.569 | 8.569 | 8.569 | 8.569 | 8.569 | 8.569 | 8.569 | 8.569 | 8.569 | 8.569 | 8.569 | 8.569 | 8.569 | 8.569 | 8.569 | 8.569 | 8.569 | 8.569 | 8.569 | 8.569 | -0.1%
Pumped Storage/Other | Electricity: Electric Power Sector: Generation: Pumped Storage/Other: Reference case without Clean Power Plan | 62-AEO2016.85.ref_no_cpp-d032316a | BkWh | 0.0006 | 0.0006 | 0.0006 | 0.0006 | 0.001377 | 0.001377 | 0.001377 | 0.001377 | 0.001377 | 0.001377 | 0.001377 | 0.001377 | 0.001669 | 0.001976 | 0.002129 | 0.002232 | 0.002312 | 0.002312 | 0.002519 | 0.002618 | 0.002716 | 0.003197 | 0.003283 | 0.003384 | 0.003403 | 0.003486 | 0.003506 | 7.3%
Renewable Sources | Electricity: Electric Power Sector: Generation: Renewable Sources: Reference case without Clean Power Plan | 62-AEO2016.86.ref_no_cpp-d032316a | BkWh | 11.0204 | 11.192 | 13.7174 | 14.7866 | 17.3954 | 21.6767 | 25.4914 | 28.1431 | 28.6297 | 28.632 | 28.6408 | 28.7808 | 28.9713 | 29.1994 | 29.4155 | 29.6525 | 29.9099 | 29.9472 | 30.0541 | 30.2175 | 30.4556 | 30.5058 | 30.6167 | 30.6444 | 30.7904 | 30.8218 | 30.9401 | 4.2%
Distributed Generation | Electricity: Electric Power Sector: Generation: Distributed Generation: Reference case without Clean Power Plan | 62-AEO2016.87.ref_no_cpp-d032316a | BkWh | [27 empty] | - -
Total Generation | Electricity: Electric Power Sector: Generation: Total Generation: Reference case without Clean Power Plan | 62-AEO2016.88.ref_no_cpp-d032316a | BkWh | 71.1824 | 65.0782 | 67.0481 | 72.2447 | 73.7891 | 81.0935 | 85.1408 | 87.8462 | 86.3548 | 89.0561 | 89.4733 | 90.0719 | 90.3232 | 90.6718 | 90.6834 | 90.9547 | 90.6278 | 90.6976 | 90.7239 | 91.6155 | 92.1757 | 92.2356 | 92.4201 | 92.3775 | 92.5062 | 92.4377 | 92.5508 | 1.4%
Sales to Customers | Electricity: Electric Power Sector: Generation: Sales to Customers: Reference case without Clean Power Plan | 62-AEO2016.89.ref_no_cpp-d032316a | BkWh | 71.1824 | 65.0125 | 66.9824 | 72.179 | 73.7234 | 81.0278 | 85.0751 | 87.7806 | 86.2891 | 88.9904 | 89.4077 | 90.0062 | 90.2576 | 90.6061 | 90.6178 | 90.889 | 90.5621 | 90.6319 | 90.6582 | 91.5498 | 92.1101 | 92.17 | 92.3545 | 92.3119 | 92.4405 | 92.372 | 92.4852 | 1.4%
Generation for Own Use | Electricity: Electric Power Sector: Generation: Generation for Own Use: Reference case without Clean Power Plan | 62-AEO2016.90.ref_no_cpp-d032316a | BkWh |  | 0.06567 | 0.06567 | 0.06567 | 0.06567 | 0.06567 | 0.06567 | 0.06567 | 0.06567 | 0.06567 | 0.06567 | 0.06567 | 0.06567 | 0.06567 | 0.06567 | 0.06567 | 0.06567 | 0.06567 | 0.06567 | 0.06567 | 0.06567 | 0.06567 | 0.06567 | 0.06567 | 0.06567 | 0.06567 | 0.06567 | 0%
End-Use Sectors |  | 62-AEO2016.93.
Coal | Electricity: End-Use Sectors: Generation: Coal: Reference case without Clean Power Plan | 62-AEO2016.94.ref_no_cpp-d032316a | BkWh | [27 empty] | - -
Petroleum | Electricity: End-Use Sectors: Generation: Petroleum: Reference case without Clean Power Plan | 62-AEO2016.95.ref_no_cpp-d032316a | BkWh | [27 empty] | - -
Natural Gas | Electricity: End-Use Sectors: Generation: Natural Gas: Reference case without Clean Power Plan | 62-AEO2016.96.ref_no_cpp-d032316a | BkWh | 0.091873 | 0.10298 | 0.11526 | 0.12464 | 0.16106 | 0.16996 | 0.17905 | 0.189 | 0.19969 | 0.21116 | 0.22362 | 0.23745 | 0.25307 | 0.27033 | 0.28883 | 0.30897 | 0.33126 | 0.35444 | 0.37797 | 0.40228 | 0.42768 | 0.4545 | 0.47643 | 0.49456 | 0.51019 | 0.52518 | 0.541 | 6.9%
Other Gaseous Fuels | Electricity: End-Use Sectors: Generation: Other Gaseous Fuels: Reference case without Clean Power Plan | 62-AEO2016.97.ref_no_cpp-d032316a | BkWh | [27 empty] | - -
Renewable Sources | Electricity: End-Use Sectors: Generation: Renewable Sources: Reference case without Clean Power Plan | 62-AEO2016.98.ref_no_cpp-d032316a | BkWh | 0.00559 | 0.014099 | 0.024426 | 0.03494 | 0.047019 | 0.060164 | 0.073681 | 0.087493 | 0.093516 | 0.095132 | 0.09728 | 0.10028 | 0.10386 | 0.10807 | 0.1128 | 0.11794 | 0.12361 | 0.12958 | 0.1358 | 0.14209 | 0.14846 | 0.15501 | 0.16149 | 0.16799 | 0.17455 | 0.18114 | 0.18778 | 10.9%
Other | Electricity: End-Use Sectors: Generation: Other: Reference case without Clean Power Plan | 62-AEO2016.99.ref_no_cpp-d032316a | BkWh | [27 empty] | - -
Total | Electricity: End-Use Sectors: Generation: Total: Reference case without Clean Power Plan | 62-AEO2016.100.ref_no_cpp-d032316a | BkWh | 0.097463 | 0.11708 | 0.13968 | 0.15958 | 0.20808 | 0.23013 | 0.25273 | 0.27649 | 0.29321 | 0.30629 | 0.3209 | 0.33773 | 0.35692 | 0.3784 | 0.40162 | 0.42691 | 0.45487 | 0.48402 | 0.51377 | 0.54437 | 0.57615 | 0.60952 | 0.63792 | 0.66255 | 0.68474 | 0.70632 | 0.72878 | 7.6%
Sales to the Grid | Electricity: End-Use Sectors: Generation: Sales to the Grid: Reference case without Clean Power Plan | 62-AEO2016.101.ref_no_cpp-d032316a | BkWh | 0.058378 | 0.062395 | 0.066609 | 0.070044 | 0.070384 | 0.074072 | 0.078036 | 0.08251 | 0.086714 | 0.090649 | 0.094931 | 0.099676 | 0.10486 | 0.1104 | 0.11609 | 0.12208 | 0.12865 | 0.13543 | 0.14216 | 0.14918 | 0.15661 | 0.16471 | 0.17222 | 0.17941 | 0.18652 | 0.19427 | 0.20328 | 4.8%
Generation for Own Use | Electricity: End-Use Sectors: Generation: Generation for Own Use: Reference case without Clean Power Plan | 62-AEO2016.102.ref_no_cpp-d032316a | BkWh | 0.039086 | 0.054687 | 0.073073 | 0.089533 | 0.1377 | 0.15605 | 0.17469 | 0.19398 | 0.20649 | 0.21564 | 0.22597 | 0.23805 | 0.25206 | 0.268 | 0.28554 | 0.30483 | 0.32622 | 0.34859 | 0.37161 | 0.39519 | 0.41954 | 0.44481 | 0.4657 | 0.48314 | 0.49823 | 0.51205 | 0.5255 | 9.5%
Total Electricity Generation | Electricity: Total Electricity Generation: Reference case without Clean Power Plan | 62-AEO2016.104.ref_no_cpp-d032316a | BkWh | 71.2798 | 65.1953 | 67.1877 | 72.4043 | 73.9971 | 81.3236 | 85.3935 | 88.1227 | 86.648 | 89.3624 | 89.7942 | 90.4096 | 90.6801 | 91.0502 | 91.0851 | 91.3816 | 91.0826 | 91.1816 | 91.2376 | 92.1599 | 92.7519 | 92.8452 | 93.0581 | 93.0401 | 93.1909 | 93.144 | 93.2796 | 1.4%
End-Use Prices |  | 62-AEO2016.106.
(2015 cents per kilowatthour) |  | 62-AEO2016.107.
Residential | Electricity: End-Use Prices: Residential: Reference case without Clean Power Plan | 62-AEO2016.108.ref_no_cpp-d032316a | 2015 cents/kWh | 12.0917 | 12.1965 | 12.2438 | 12.0599 | 12.137 | 12.223 | 12.0819 | 11.9107 | 11.7605 | 11.6154 | 11.5267 | 11.4915 | 11.4324 | 11.4539 | 11.4392 | 11.4383 | 11.483 | 11.5334 | 11.5291 | 11.4144 | 11.2618 | 11.2248 | 11.1931 | 11.1681 | 11.1461 | 11.119 | 11.1175 | -0.4%
Commercial | Electricity: End-Use Prices: Commercial: Reference case without Clean Power Plan | 62-AEO2016.109.ref_no_cpp-d032316a | 2015 cents/kWh | 10.0359 | 9.6888 | 9.6867 | 9.6305 | 9.7172 | 9.7714 | 9.6049 | 9.4576 | 9.3132 | 9.1593 | 9.0598 | 9.0044 | 8.9336 | 8.9435 | 8.925 | 8.9167 | 8.9467 | 8.9839 | 8.9713 | 8.8582 | 8.7093 | 8.6743 | 8.6407 | 8.6133 | 8.5857 | 8.5598 | 8.5554 | -0.5%
Industrial | Electricity: End-Use Prices: Industrial: Reference case without Clean Power Plan | 62-AEO2016.110.ref_no_cpp-d032316a | 2015 cents/kWh | 7.8536 | 7.537 | 7.4786 | 7.4429 | 7.5331 | 7.5394 | 7.419 | 7.3248 | 7.2272 | 7.102 | 7.0304 | 6.9935 | 6.9879 | 7.0264 | 7.0296 | 7.0584 | 7.1259 | 7.1797 | 7.188 | 7.1233 | 7.0413 | 7.0283 | 7.0173 | 7.0058 | 7.0006 | 6.9955 | 7.0046 | -0.3%
Transportation | Electricity: End-Use Prices: Transportation: Reference case without Clean Power Plan | 62-AEO2016.111.ref_no_cpp-d032316a | 2015 cents/kWh | 11.3223 | 13.1134 | 13.9586 | 14.3929 | 14.6608 | 15.0177 | 14.9215 | 14.7981 | 14.6807 | 14.5665 | 14.4723 | 14.4217 | 14.1954 | 14.1536 | 14.0874 | 13.9844 | 13.9149 | 13.9091 | 13.8367 | 13.5735 | 13.2092 | 13.1062 | 12.9995 | 12.9223 | 12.8259 | 12.7347 | 12.6885 | -0.1%
All Sectors Average | Electricity: End-Use Prices: All Sectors Average: Reference case without Clean Power Plan | 62-AEO2016.112.ref_no_cpp-d032316a | 2015 cents/kWh | 10.2488 | 10.0386 | 10.077 | 9.9796 | 10.0745 | 10.1104 | 9.942 | 9.7848 | 9.6425 | 9.4917 | 9.3999 | 9.3534 | 9.3013 | 9.3223 | 9.3147 | 9.321 | 9.3671 | 9.4153 | 9.4126 | 9.312 | 9.1795 | 9.1519 | 9.1256 | 9.1039 | 9.083 | 9.0628 | 9.0635 | -0.4%
(nominal cents per kilowatthour) |  | 62-AEO2016.113.
Residential | Electricity: End-Use Prices: Residential: Reference case without Clean Power Plan | 62-AEO2016.114.ref_no_cpp-d032316a | nom cents/kWh | 11.9667 | 12.1965 | 12.4702 | 12.54 | 12.8673 | 13.217 | 13.346 | 13.4511 | 13.5642 | 13.6615 | 13.81 | 14.0246 | 14.2206 | 14.5275 | 14.8011 | 15.1084 | 15.4945 | 15.911 | 16.2677 | 16.4791 | 16.6365 | 16.9633 | 17.2969 | 17.6396 | 17.9927 | 18.3355 | 18.717 | 1.7%
Commercial | Electricity: End-Use Prices: Commercial: Reference case without Clean Power Plan | 62-AEO2016.115.ref_no_cpp-d032316a | nom cents/kWh | 9.9321 | 9.6888 | 9.8659 | 10.0138 | 10.3019 | 10.5661 | 10.6099 | 10.6807 | 10.7416 | 10.7728 | 10.8545 | 10.9894 | 11.1124 | 11.3434 | 11.548 | 11.7777 | 12.0722 | 12.3938 | 12.6586 | 12.7887 | 12.8658 | 13.109 | 13.3526 | 13.6043 | 13.8595 | 14.1153 | 14.4035 | 1.6%
Industrial | Electricity: End-Use Prices: Industrial: Reference case without Clean Power Plan | 62-AEO2016.116.ref_no_cpp-d032316a | nom cents/kWh | 7.7724 | 7.537 | 7.6169 | 7.7391 | 7.9864 | 8.1526 | 8.1953 | 8.2721 | 8.3357 | 8.3531 | 8.4231 | 8.5352 | 8.6922 | 8.9119 | 9.0955 | 9.3231 | 9.6153 | 9.9049 | 10.1423 | 10.284 | 10.4017 | 10.6214 | 10.8439 | 11.0654 | 11.3007 | 11.5358 | 11.7928 | 1.8%
Transportation | Electricity: End-Use Prices: Transportation: Reference case without Clean Power Plan | 62-AEO2016.117.ref_no_cpp-d032316a | nom cents/kWh | 11.2052 | 13.1134 | 14.2168 | 14.9658 | 15.5429 | 16.2391 | 16.4827 | 16.7118 | 16.9323 | 17.1325 | 17.3392 | 17.6007 | 17.6575 | 17.9516 | 18.2275 | 18.4714 | 18.776 | 19.1886 | 19.5237 | 19.5962 | 19.5134 | 19.8066 | 20.0883 | 20.4102 | 20.7042 | 20.9997 | 21.3619 | 2%
All Sectors Average | Electricity: End-Use Prices: All Sectors Average: Reference case without Clean Power Plan | 62-AEO2016.118.ref_no_cpp-d032316a | nom cents/kWh | 10.1428 | 10.0386 | 10.2634 | 10.3768 | 10.6806 | 10.9326 | 10.9821 | 11.0502 | 11.1213 | 11.1636 | 11.2619 | 11.4152 | 11.5698 | 11.8238 | 12.0522 | 12.3117 | 12.6394 | 12.9891 | 13.2812 | 13.4438 | 13.5604 | 13.8307 | 14.102 | 14.3791 | 14.6624 | 14.9447 | 15.259 | 1.7%
Prices by Service Category |  | 62-AEO2016.120.
(2015 cents per kilowatthour) |  | 62-AEO2016.121.
Generation | Electricity: Prices by Service Category: Generation: Reference case without Clean Power Plan | 62-AEO2016.122.ref_no_cpp-d032316a | 2015 cents/kWh | 6.8142 | 6.5185 | 6.4393 | 6.2937 | 6.2923 | 6.2264 | 6.0419 | 5.8979 | 5.7808 | 5.6438 | 5.5563 | 5.5096 | 5.4562 | 5.4801 | 5.4709 | 5.4752 | 5.5184 | 5.5653 | 5.5649 | 5.4632 | 5.3236 | 5.2986 | 5.2696 | 5.2512 | 5.2284 | 5.21 | 5.2071 | -0.9%
Transmission | Electricity: Prices by Service Category: Transmission: Reference case without Clean Power Plan | 62-AEO2016.123.ref_no_cpp-d032316a | 2015 cents/kWh | 1.0158 | 1.0456 | 1.0904 | 1.1147 | 1.1567 | 1.2088 | 1.2306 | 1.2361 | 1.2301 | 1.2229 | 1.2189 | 1.2166 | 1.2158 | 1.2143 | 1.2136 | 1.2118 | 1.2112 | 1.2108 | 1.2075 | 1.2059 | 1.2076 | 1.2087 | 1.2135 | 1.2142 | 1.2167 | 1.2193 | 1.2227 | 0.6%
Distribution | Electricity: Prices by Service Category: Distribution: Reference case without Clean Power Plan | 62-AEO2016.124.ref_no_cpp-d032316a | 2015 cents/kWh | 2.4188 | 2.4746 | 2.5473 | 2.5711 | 2.6256 | 2.6751 | 2.6694 | 2.6507 | 2.6316 | 2.6249 | 2.6247 | 2.6271 | 2.6294 | 2.6279 | 2.6302 | 2.634 | 2.6375 | 2.6392 | 2.6401 | 2.6429 | 2.6484 | 2.6446 | 2.6425 | 2.6385 | 2.6379 | 2.6334 | 2.6336 | 0.2%
(nominal cents per kilowatthour) |  | 62-AEO2016.125.
Generation | Electricity: Prices by Service Category: Generation: Reference case without Clean Power Plan | 62-AEO2016.126.ref_no_cpp-d032316a | nom cents/kWh | 6.7438 | 6.5185 | 6.5584 | 6.5443 | 6.6708 | 6.7328 | 6.6741 | 6.6607 | 6.6674 | 6.638 | 6.657 | 6.7241 | 6.7868 | 6.9507 | 7.0787 | 7.232 | 7.4462 | 7.6777 | 7.8521 | 7.8873 | 7.8642 | 8.0074 | 8.1432 | 8.2941 | 8.44 | 8.5914 | 8.7665 | 1.2%
Transmission | Electricity: Prices by Service Category: Transmission: Reference case without Clean Power Plan | 62-AEO2016.127.ref_no_cpp-d032316a | nom cents/kWh | 1.0053 | 1.0456 | 1.1106 | 1.1591 | 1.2263 | 1.3072 | 1.3594 | 1.396 | 1.4188 | 1.4383 | 1.4604 | 1.4848 | 1.5123 | 1.5401 | 1.5703 | 1.6006 | 1.6343 | 1.6704 | 1.7038 | 1.7409 | 1.7839 | 1.8267 | 1.8752 | 1.9177 | 1.964 | 2.0107 | 2.0586 | 2.7%
Distribution | Electricity: Prices by Service Category: Distribution: Reference case without Clean Power Plan | 62-AEO2016.128.ref_no_cpp-d032316a | nom cents/kWh | 2.3937 | 2.4746 | 2.5944 | 2.6735 | 2.7835 | 2.8926 | 2.9487 | 2.9935 | 3.0352 | 3.0873 | 3.1446 | 3.2063 | 3.2707 | 3.333 | 3.4032 | 3.4791 | 3.5589 | 3.641 | 3.7252 | 3.8156 | 3.9123 | 3.9967 | 4.0836 | 4.1673 | 4.2583 | 4.3426 | 4.4339 | 2.4%
Fuel Consumption (quadrillion Btu) |  | 62-AEO2016.130.
Coal | Electricity: Fuel Use: Coal: Reference case without Clean Power Plan | 62-AEO2016.131.ref_no_cpp-d032316a | quads | 0.50483 | 0.43988 | 0.4398 | 0.49106 | 0.48063 | 0.50688 | 0.50795 | 0.50603 | 0.48153 | 0.5108 | 0.51319 | 0.51696 | 0.51693 | 0.51425 | 0.51249 | 0.51239 | 0.50602 | 0.50588 | 0.50574 | 0.50792 | 0.50778 | 0.50765 | 0.5075 | 0.50735 | 0.50723 | 0.50708 | 0.50696 | 0.6%
Natural Gas | Electricity: Fuel Use: Natural Gas: Reference case without Clean Power Plan | 62-AEO2016.132.ref_no_cpp-d032316a | quads | 0.045575 | 0.033181 | 0.030979 | 0.022322 | 0.021395 | 0.027285 | 0.029338 | 0.03143 | 0.033642 | 0.03331 | 0.03497 | 0.036038 | 0.036446 | 0.039658 | 0.039164 | 0.03939 | 0.038757 | 0.03876 | 0.038386 | 0.043287 | 0.045509 | 0.04551 | 0.045942 | 0.045425 | 0.045305 | 0.044584 | 0.044645 | 1.2%
Oil | Electricity: Fuel Use: Oil: Reference case without Clean Power Plan | 62-AEO2016.133.ref_no_cpp-d032316a | quads | 0.001494 | 0.001767 | 0.001768 | 0.001981 | 0.001939 | 0.002044 | 0.002047 | 0.002039 | 0.001956 | 0.002074 | 0.002084 | 0.002099 | 0.002099 | 0.002089 | 0.002081 | 0.002081 | 0.002056 | 0.002055 | 0.002054 | 0.002063 | 0.002063 | 0.002062 | 0.002061 | 0.002061 | 0.00206 | 0.00206 | 0.002059 | 0.6%
Total | Electricity: Fuel Use: Total: Reference case without Clean Power Plan | 62-AEO2016.134.ref_no_cpp-d032316a | quads | 0.5519 | 0.47483 | 0.47255 | 0.51536 | 0.50397 | 0.53621 | 0.53933 | 0.5395 | 0.51713 | 0.54619 | 0.55024 | 0.55509 | 0.55548 | 0.556 | 0.55373 | 0.55386 | 0.54683 | 0.54669 | 0.54618 | 0.55327 | 0.55535 | 0.55523 | 0.5555 | 0.55483 | 0.55459 | 0.55373 | 0.55366 | 0.6%
Fuel Prices to the Electric Power Sector |  | 62-AEO2016.136.
(2015 dollars per million Btu) |  | 62-AEO2016.137.
Coal | Electricity: Fuel Prices: Coal: Reference case without Clean Power Plan | 62-AEO2016.138.ref_no_cpp-d032316a | 2015 $/MMBtu | 1.9619 | 1.8663 | 1.6635 | 1.6418 | 1.8272 | 1.8394 | 1.8529 | 1.884 | 1.9083 | 1.9392 | 1.9662 | 1.9913 | 2.0205 | 2.0515 | 2.0865 | 2.1198 | 2.153 | 2.1885 | 2.221 | 2.2435 | 2.2726 | 2.2926 | 2.3164 | 2.3387 | 2.3627 | 2.3835 | 2.4118 | 1%
Natural Gas | Electricity: Fuel Prices: Natural Gas: Reference case without Clean Power Plan | 62-AEO2016.139.ref_no_cpp-d032316a | 2015 $/MMBtu | 5.5544 | 3.2131 | 3.7092 | 4.1411 | 4.439 | 4.7595 | 5.0775 | 5.2121 | 5.2847 | 5.5037 | 5.6513 | 5.814 | 5.8133 | 5.7014 | 5.6478 | 5.593 | 5.5677 | 5.5866 | 5.7088 | 5.7571 | 5.8023 | 5.7969 | 5.7148 | 5.7355 | 5.7607 | 5.7682 | 5.6977 | 2.3%
Distillate Fuel Oil | Electricity: Fuel Prices: Distillate Fuel Oil: Reference case without Clean Power Plan | 62-AEO2016.140.ref_no_cpp-d032316a | 2015 $/MMBtu | 24.1863 | 15.1531 | 11.6901 | 13.2292 | 14.4977 | 16.4068 | 17.0264 | 17.3755 | 17.5171 | 17.9466 | 18.3317 | 18.7903 | 19.3779 | 19.8468 | 20.2357 | 20.7067 | 21.0457 | 21.6359 | 22.2546 | 22.8644 | 23.6134 | 23.9979 | 24.6694 | 25.0814 | 25.7589 | 26.4317 | 27.0774 | 2.3%
Residual Fuel Oil | Electricity: Fuel Prices: Residual Fuel Oil: Reference case without Clean Power Plan | 62-AEO2016.141.ref_no_cpp-d032316a | 2015 $/MMBtu | 11.9012 | 4.6753 | 2.582 | 4.4471 | 5.3912 | 7.3571 | 8.3361 | 9.0832 | 9.6624 | 10.0691 | 10.4071 | 10.7937 | 11.3208 | 11.6891 | 11.9621 | 12.2857 | 12.5394 | 13.025 | 13.5512 | 14.0872 | 14.7396 | 14.9802 | 15.5663 | 15.8652 | 16.4211 | 17.0549 | 17.5835 | 5.4%
(nominal dollars per million Btu) |  | 62-AEO2016.143.
Coal | Electricity: Fuel Prices: Coal: Reference case without Clean Power Plan | 62-AEO2016.144.ref_no_cpp-d032316a | nom $/MMBtu | 1.9417 | 1.8663 | 1.6943 | 1.7072 | 1.9372 | 1.989 | 2.0468 | 2.1276 | 2.201 | 2.2807 | 2.3557 | 2.4302 | 2.5132 | 2.6021 | 2.6998 | 2.7999 | 2.9051 | 3.0191 | 3.1339 | 3.239 | 3.3572 | 3.4647 | 3.5796 | 3.6939 | 3.8141 | 3.9304 | 4.0604 | 3.2%
Natural Gas | Electricity: Fuel Prices: Natural Gas: Reference case without Clean Power Plan | 62-AEO2016.145.ref_no_cpp-d032316a | nom $/MMBtu | 5.4969 | 3.2131 | 3.7778 | 4.3059 | 4.7061 | 5.1465 | 5.6088 | 5.8861 | 6.0952 | 6.4732 | 6.7708 | 7.0956 | 7.2311 | 7.2313 | 7.3076 | 7.3876 | 7.5127 | 7.707 | 8.0551 | 8.3116 | 8.5714 | 8.7605 | 8.8312 | 9.0589 | 9.2993 | 9.5118 | 9.5925 | 4.5%
[5 empty] | -41.55% | 17.58% | 13.98% | 9.293% | 9.36% | 8.982% | 4.945% | 3.552% | 6.201% | 4.598% | 4.797% | 1.908% | 0.00289% | 1.056% | 1.094% | 1.694% | 2.586% | 4.517% | 3.184% | 3.126% | 2.206% | 0.8074% | 2.579% | 2.653% | 2.285% | 0.849% | 2.78%
Distillate Fuel Oil | Electricity: Fuel Prices: Distillate Fuel Oil: Reference case without Clean Power Plan | 62-AEO2016.146.ref_no_cpp-d032316a | nom $/MMBtu | 23.9362 | 15.1531 | 11.9062 | 13.7558 | 15.3699 | 17.7412 | 18.8078 | 19.6226 | 20.2036 | 21.108 | 21.9631 | 22.9324 | 24.1039 | 25.1725 | 26.1827 | 27.3506 | 28.3979 | 29.8481 | 31.4014 | 33.0095 | 34.8829 | 36.2665 | 38.1221 | 39.6149 | 41.5814 | 43.5864 | 45.5866 | 4.5%
Residual Fuel Oil | Electricity: Fuel Prices: Residual Fuel Oil: Reference case without Clean Power Plan | 62-AEO2016.147.ref_no_cpp-d032316a | nom $/MMBtu | 11.7782 | 4.6753 | 2.6298 | 4.6241 | 5.7156 | 7.9554 | 9.2082 | 10.2578 | 11.1443 | 11.8428 | 12.4687 | 13.173 | 14.0818 | 14.8258 | 15.4777 | 16.2276 | 16.92 | 17.9689 | 19.1208 | 20.3379 | 21.7742 | 22.6386 | 24.0549 | 25.0584 | 26.5079 | 28.1239 | 29.603 | 7.7%
Emissions from the Electric Power Sector |  | 62-AEO2016.150.
Total Carbon (million short tons) | Electricity: Emissions: Total Carbon: Reference case without Clean Power Plan | 62-AEO2016.151.ref_no_cpp-d032316a | MMst | 15.2128 | 13.5322 | 13.4892 | 14.8651 | 14.5412 | 15.4096 | 15.4743 | 15.4518 | 14.762 | 15.6205 | 15.7157 | 15.8423 | 15.8647 | 15.8178 | 15.7601 | 15.7566 | 15.5733 | 15.552 | 15.5449 | 15.6835 | 15.7344 | 15.7091 | 15.652 | 15.6213 | 15.6134 | 15.5878 | 15.6035 | 0.6%
Carbon Dioxide (million short tons) | Electricity: Emissions: Carbon Dioxide: Reference case without Clean Power Plan | 62-AEO2016.152.ref_no_cpp-d032316a | MMst | 55.7804 | 49.618 | 49.4604 | 54.5054 | 53.3178 | 56.5019 | 56.739 | 56.6566 | 54.1273 | 57.2752 | 57.6242 | 58.0885 | 58.1704 | 57.9985 | 57.7872 | 57.7742 | 57.1022 | 57.0241 | 56.9981 | 57.506 | 57.6927 | 57.5998 | 57.3907 | 57.2782 | 57.2493 | 57.1554 | 57.2129 | 0.6%
Sulfur Dioxide (million short tons) | Electricity: Emissions: Sulfur Dioxide: Reference case without Clean Power Plan | 62-AEO2016.153.ref_no_cpp-d032316a | MMst | 0.071216 | 0.021023 | 0.01073 | 0.017159 | 0.014931 | 0.017411 | 0.01348 | 0.016655 | 0.011317 | 0.013026 | 0.012696 | 0.013925 | 0.015501 | 0.013609 | 0.01298 | 0.013471 | 0.01432 | 0.01169 | 0.01243 | 0.01197 | 0.01489 | 0.012671 | 0.013271 | 0.013344 | 0.014145 | 0.013434 | 0.01465 | -1.4%
Nitrogen Oxide (million short tons) | Electricity: Emissions: Nitrogen Oxide: Reference case without Clean Power Plan | 62-AEO2016.154.ref_no_cpp-d032316a | MMst | 0.04 | 0.037564 | 0.034094 | 0.040539 | 0.039635 | 0.043082 | 0.042807 | 0.042603 | 0.038849 | 0.040389 | 0.040046 | 0.041237 | 0.041329 | 0.041063 | 0.040854 | 0.040733 | 0.039563 | 0.039414 | 0.03947 | 0.040096 | 0.040184 | 0.040059 | 0.040304 | 0.040115 | 0.04009 | 0.039956 | 0.039876 | 0.2%
Mercury (short tons) | Electricity: Emissions: Mercury: Reference case without Clean Power Plan | 62-AEO2016.155.ref_no_cpp-d032316a | st | 0.70969 | 0.66208 | 0.1488 | 0.16695 | 0.16572 | 0.17455 | 0.17478 | 0.17525 | 0.16564 | 0.17614 | 0.17551 | 0.17802 | 0.16991 | 0.17729 | 0.17409 | 0.17657 | 0.16676 | 0.17408 | 0.17174 | 0.17405 | 0.16461 | 0.17461 | 0.16007 | 0.15279 | 0.14902 | 0.15404 | 0.14563 | -5.9%

## Forward Market Price Table
| PEAK | OFF PEAK | FLAT | PEAK | OFF PEAK
2017 | 28.8625 | 17.7875 | 22.941 | 46.53% | 53.47%
2018 | 27.3083 | 18.075 | 22.3715
2019 | 29.8643 | 19.7668 | 24.4655
2020 | 32.5467 | 21.5422 | 26.6629
2021 | 34.1561 | 22.6074 | 27.9814
2022 | 35.3695 | 23.4106 | 28.9754
2023 | 37.5626 | 24.8622 | 30.7721
2024 | 39.2899 | 26.0054 | 32.187
2025 | 41.1746 | 27.2529 | 33.7311
2026 | 41.9604 | 27.773 | 34.3748
2027 | 41.9616 | 27.7738 | 34.3758
2028 | 42.4047 | 28.0671 | 34.7388
2029 | 42.8685 | 28.3741 | 35.1187
2030 | 43.5949 | 28.8548 | 35.7138
2031 | 44.7224 | 29.6011 | 36.6375
2032 | 46.7424 | 30.9381 | 38.2923
2033 | 48.2305 | 31.9231 | 39.5114
2034 | 49.7381 | 32.9209 | 40.7464
2035 | 50.8355 | 33.6473 | 41.6454
2036 | 51.2459 | 33.919 | 41.9817

## Forward Curve
Date | On Peak | Off Peak
2017-01-01 | 31.45 | 25.25
2017-02-01 | 31.5 | 22
2017-03-01 | 30 | 17.9
2017-04-01 | 27.75 | 14
2017-05-01 | 27.45 | 15.95
2017-06-01 | 26.45 | 15.55
2017-07-01 | 36.2 | 17.85
2017-08-01 | 32.7 | 15.55
2017-09-01 | 28.8 | 16.1
2017-10-01 | 23.85 | 17.05
2017-11-01 | 23.8 | 16.3
2017-12-01 | 26.4 | 19.95
2018-01-01 | 35.05 | 26.45
2018-02-01 | 32.65 | 24.1
2018-03-01 | 26.9 | 19.55
2018-04-01 | 24.45 | 18.45
2018-05-01 | 25.3 | 14.55
2018-06-01 | 25.1 | 15.2
2018-07-01 | 31.7 | 16.85
2018-08-01 | 28.8 | 16.5
2018-09-01 | 24.25 | 14.5
2018-10-01 | 24.4 | 16.1
2018-11-01 | 24.3 | 16.95
2018-12-01 | 24.8 | 17.7
2019-01-01 | 38.3306 | 28.9257
2019-02-01 | 35.706 | 26.3557
2019-03-01 | 29.4178 | 21.3798
2019-04-01 | 26.7385 | 20.1769
2019-05-01 | 27.668 | 15.9119
2019-06-01 | 27.4493 | 16.6227
2019-07-01 | 34.6671 | 18.4271
2019-08-01 | 31.4956 | 18.0444
2019-09-01 | 26.5198 | 15.8572
2019-10-01 | 26.6838 | 17.6069
2019-11-01 | 26.5744 | 18.5365
2019-12-01 | 27.1212 | 19.3567
2020-01-01 | 41.7733 | 31.5237
2020-02-01 | 38.913 | 28.7229
2020-03-01 | 32.06 | 23.3001
2020-04-01 | 29.14 | 21.9891
2020-05-01 | 30.1531 | 17.341
2020-06-01 | 29.9147 | 18.1157
2020-07-01 | 37.7807 | 20.0822
2020-08-01 | 34.3245 | 19.6651
2020-09-01 | 28.9017 | 17.2814
2020-10-01 | 29.0804 | 19.1883
2020-11-01 | 28.9613 | 20.2014
2020-12-01 | 29.5572 | 21.0952
2021-01-01 | 43.839 | 33.0825
2021-02-01 | 40.8372 | 30.1432
2021-03-01 | 33.6454 | 24.4523
2021-04-01 | 30.581 | 23.0765
2021-05-01 | 31.6442 | 18.1985
2021-06-01 | 31.394 | 19.0115
2021-07-01 | 39.649 | 21.0753
2021-08-01 | 36.0218 | 20.6375
2021-09-01 | 30.3309 | 18.136
2021-10-01 | 30.5185 | 20.1372
2021-11-01 | 30.3934 | 21.2003
2021-12-01 | 31.0188 | 22.1384
2022-01-01 | 45.3964 | 34.2578
2022-02-01 | 42.2879 | 31.2141
2022-03-01 | 34.8406 | 25.321
2022-04-01 | 31.6674 | 23.8963
2022-05-01 | 32.7683 | 18.845
2022-06-01 | 32.5093 | 19.6869
2022-07-01 | 41.0575 | 21.8239
2022-08-01 | 37.3015 | 21.3706
2022-09-01 | 31.4084 | 18.7803
2022-10-01 | 31.6026 | 20.8526
2022-11-01 | 31.4731 | 21.9535
2022-12-01 | 32.1207 | 22.9249
2023-01-01 | 48.2113 | 36.382
2023-02-01 | 44.9101 | 33.1496
2023-03-01 | 37.001 | 26.891
2023-04-01 | 33.631 | 25.378
2023-05-01 | 34.8002 | 20.0135
2023-06-01 | 34.5251 | 20.9076
2023-07-01 | 43.6034 | 23.1772
2023-08-01 | 39.6144 | 22.6958
2023-09-01 | 33.3559 | 19.9448
2023-10-01 | 33.5622 | 22.1456
2023-11-01 | 33.4247 | 23.3147
2023-12-01 | 34.1124 | 24.3464
2024-01-01 | 50.4282 | 38.0549
2024-02-01 | 46.9752 | 34.6739
2024-03-01 | 38.7024 | 28.1276
2024-04-01 | 35.1774 | 26.5449
2024-05-01 | 36.4004 | 20.9338
2024-06-01 | 36.1126 | 21.869
2024-07-01 | 45.6084 | 24.2429
2024-08-01 | 41.436 | 23.7394
2024-09-01 | 34.8897 | 20.8619
2024-10-01 | 35.1055 | 23.1639
2024-11-01 | 34.9616 | 24.3868
2024-12-01 | 35.681 | 25.4659
2025-01-01 | 52.8473 | 39.8805
2025-02-01 | 49.2286 | 36.3372
2025-03-01 | 40.559 | 29.4769
2025-04-01 | 36.8649 | 27.8183
2025-05-01 | 38.1465 | 21.938
2025-06-01 | 37.845 | 22.9181
2025-07-01 | 47.7963 | 25.4059
2025-08-01 | 43.4237 | 24.8782
2025-09-01 | 36.5634 | 21.8626
2025-10-01 | 36.7896 | 24.2751
2025-11-01 | 36.6388 | 25.5567
2025-12-01 | 37.3927 | 26.6875
2026-01-01 | 53.8558 | 40.6416
2026-02-01 | 50.1681 | 37.0307
2026-03-01 | 41.333 | 30.0394
2026-04-01 | 37.5685 | 28.3492
2026-05-01 | 38.8745 | 22.3567
2026-06-01 | 38.5672 | 23.3554
2026-07-01 | 48.7084 | 25.8907
2026-08-01 | 44.2524 | 25.353
2026-09-01 | 37.2612 | 22.2799
2026-10-01 | 37.4916 | 24.7383
2026-11-01 | 37.338 | 26.0444
2026-12-01 | 38.1063 | 27.1968
2027-01-01 | 53.8574 | 40.6427
2027-02-01 | 50.1696 | 37.0317
2027-03-01 | 41.3342 | 30.0403
2027-04-01 | 37.5696 | 28.35
2027-05-01 | 38.8757 | 22.3573
2027-06-01 | 38.5683 | 23.3561
2027-07-01 | 48.7098 | 25.8915
2027-08-01 | 44.2537 | 25.3537
2027-09-01 | 37.2622 | 22.2805
2027-10-01 | 37.4927 | 24.7391
2027-11-01 | 37.3391 | 26.0452
2027-12-01 | 38.1074 | 27.1976
2028-01-01 | 54.4261 | 41.0719
2028-02-01 | 50.6993 | 37.4228
2028-03-01 | 41.7707 | 30.3575
2028-04-01 | 37.9663 | 28.6494
2028-05-01 | 39.2862 | 22.5934
2028-06-01 | 38.9756 | 23.6027
2028-07-01 | 49.2242 | 26.1649
2028-08-01 | 44.721 | 25.6214
2028-09-01 | 37.6557 | 22.5158
2028-10-01 | 37.8886 | 25.0003
2028-11-01 | 37.7333 | 26.3202
2028-12-01 | 38.5097 | 27.4848
2029-01-01 | 55.0213 | 41.5211
2029-02-01 | 51.2538 | 37.8321
2029-03-01 | 42.2275 | 30.6895
2029-04-01 | 38.3815 | 28.9627
2029-05-01 | 39.7158 | 22.8405
2029-06-01 | 39.4019 | 23.8609
2029-07-01 | 49.7625 | 26.4511
2029-08-01 | 45.2101 | 25.9016
2029-09-01 | 38.0676 | 22.762
2029-10-01 | 38.303 | 25.2737
2029-11-01 | 38.146 | 26.608
2029-12-01 | 38.9309 | 27.7854
2030-01-01 | 55.9537 | 42.2247
2030-02-01 | 52.1223 | 38.4731
2030-03-01 | 42.943 | 31.2095
2030-04-01 | 39.0319 | 29.4535
2030-05-01 | 40.3888 | 23.2276
2030-06-01 | 40.0695 | 24.2652
2030-07-01 | 50.6057 | 26.8993
2030-08-01 | 45.9762 | 26.3405
2030-09-01 | 38.7126 | 23.1477
2030-10-01 | 38.952 | 25.702
2030-11-01 | 38.7924 | 27.0589
2030-12-01 | 39.5906 | 28.2562
2031-01-01 | 57.4008 | 43.3167
2031-02-01 | 53.4704 | 39.4682
2031-03-01 | 44.0537 | 32.0167
2031-04-01 | 40.0414 | 30.2153
2031-05-01 | 41.4334 | 23.8283
2031-06-01 | 41.1059 | 24.8928
2031-07-01 | 51.9146 | 27.595
2031-08-01 | 47.1653 | 27.0218
2031-09-01 | 39.7138 | 23.7464
2031-10-01 | 39.9595 | 26.3667
2031-11-01 | 39.7957 | 27.7587
2031-12-01 | 40.6146 | 28.987
2032-01-01 | 59.9935 | 45.2732
2032-02-01 | 55.8855 | 41.2509
2032-03-01 | 46.0435 | 33.4628
2032-04-01 | 41.8499 | 31.58
2032-05-01 | 43.3048 | 24.9046
2032-06-01 | 42.9625 | 26.0171
2032-07-01 | 54.2594 | 28.8414
2032-08-01 | 49.2956 | 28.2423
2032-09-01 | 41.5076 | 24.819
2032-10-01 | 41.7644 | 27.5576
2032-11-01 | 41.5932 | 29.0125
2032-12-01 | 42.449 | 30.2963
2033-01-01 | 61.9034 | 46.7146
2033-02-01 | 57.6647 | 42.5641
2033-03-01 | 47.5093 | 34.5282
2033-04-01 | 43.1823 | 32.5854
2033-05-01 | 44.6835 | 25.6974
2033-06-01 | 44.3303 | 26.8454
2033-07-01 | 55.9868 | 29.7596
2033-08-01 | 50.865 | 29.1414
2033-09-01 | 42.829 | 25.6091
2033-10-01 | 43.094 | 28.435
2033-11-01 | 42.9174 | 29.9362
2033-12-01 | 43.8004 | 31.2608
2034-01-01 | 63.8384 | 48.1747
2034-02-01 | 59.4671 | 43.8946
2034-03-01 | 48.9943 | 35.6074
2034-04-01 | 44.532 | 33.6039
2034-05-01 | 46.0802 | 26.5007
2034-06-01 | 45.7159 | 27.6845
2034-07-01 | 57.7368 | 30.6898
2034-08-01 | 52.4549 | 30.0523
2034-09-01 | 44.1678 | 26.4096
2034-10-01 | 44.441 | 29.3238
2034-11-01 | 44.2588 | 30.8719
2034-12-01 | 45.1695 | 32.2379
2035-01-01 | 65.2469 | 49.2377
2035-02-01 | 60.7792 | 44.8631
2035-03-01 | 50.0754 | 36.3931
2035-04-01 | 45.5146 | 34.3454
2035-05-01 | 47.0969 | 27.0854
2035-06-01 | 46.7246 | 28.2954
2035-07-01 | 59.0107 | 31.3669
2035-08-01 | 53.6123 | 30.7154
2035-09-01 | 45.1423 | 26.9923
2035-10-01 | 45.4215 | 29.9708
2035-11-01 | 45.2354 | 31.5531
2035-12-01 | 46.1661 | 32.9492
2036-01-01 | 65.7737 | 49.6352
2036-02-01 | 61.2699 | 45.2253
2036-03-01 | 50.4797 | 36.6869
2036-04-01 | 45.8821 | 34.6227
2036-05-01 | 47.4772 | 27.3041
2036-06-01 | 47.1018 | 28.5238
2036-07-01 | 59.4872 | 31.6202
2036-08-01 | 54.0451 | 30.9634
2036-09-01 | 45.5068 | 27.2102
2036-10-01 | 45.7882 | 30.2127
2036-11-01 | 45.6006 | 31.8078
2036-12-01 | 46.5389 | 33.2152
2037-01-01 | 67.4697 | 50.9151
2037-02-01 | 62.8498 | 46.3914
2037-03-01 | 51.7813 | 37.6329
2037-04-01 | 47.0652 | 35.5154
2037-05-01 | 48.7014 | 28.0081
2037-06-01 | 48.3164 | 29.2593
2037-07-01 | 61.0211 | 32.4355
2037-08-01 | 55.4387 | 31.7618
2037-09-01 | 46.6802 | 27.9118
2037-10-01 | 46.9689 | 30.9918
2037-11-01 | 46.7764 | 32.628
2037-12-01 | 47.7389 | 34.0717
2038-01-01 | 69.2598 | 52.266
2038-02-01 | 64.5174 | 47.6223
2038-03-01 | 53.1552 | 38.6314
2038-04-01 | 48.3139 | 36.4577
2038-05-01 | 49.9935 | 28.7512
2038-06-01 | 49.5983 | 30.0357
2038-07-01 | 62.6401 | 33.2961
2038-08-01 | 56.9097 | 32.6045
2038-09-01 | 47.9187 | 28.6524
2038-10-01 | 48.2151 | 31.8141
2038-11-01 | 48.0175 | 33.4937
2038-12-01 | 49.0055 | 34.9757
2039-01-01 | 70.8422 | 53.4601
2039-02-01 | 65.9914 | 48.7104
2039-03-01 | 54.3696 | 39.514
2039-04-01 | 49.4178 | 37.2907
2039-05-01 | 51.1358 | 29.4081
2039-06-01 | 50.7315 | 30.7219
2039-07-01 | 64.0713 | 34.0568
2039-08-01 | 58.2099 | 33.3494
2039-09-01 | 49.0135 | 29.3071
2039-10-01 | 49.3167 | 32.5409
2039-11-01 | 49.1146 | 34.2589
2039-12-01 | 50.1252 | 35.7748
2040-01-01 | 71.4437 | 53.914
2040-02-01 | 66.5517 | 49.1239
2040-03-01 | 54.8313 | 39.8495
2040-04-01 | 49.8373 | 37.6073
2040-05-01 | 51.5699 | 29.6578
2040-06-01 | 51.1623 | 30.9827
2040-07-01 | 64.6153 | 34.346
2040-08-01 | 58.7041 | 33.6326
2040-09-01 | 49.4297 | 29.5559
2040-10-01 | 49.7354 | 32.8172
2040-11-01 | 49.5316 | 34.5498
2040-12-01 | 50.5508 | 36.0786

## Peak
| peak | EIA Escalation
2016-09-01 | 24.04 | 2019 | 9.36% |  |  | STARTDATE | ENDDATE | SPP on pk | Aberdeen 1 | Aberdeen 2 | Beethoven | Big Stone | Coyote | Huron 1 | Huron 2 | Neal 4 | Oak Tree | Titan | Load
2016-10-01 | 23.92 | 2020 | 8.982% |  |  | 2017-01-01 | 2017-02-01 | 31.45 | 0.32503 | 31.775 | 31.64 | 31.745 | 30.9925 | 31.2825 | 31.2825 | 31.7625 | 31.7625 | 0.15503 | 32.045
2016-11-01 | 26.55 | 2021 | 4.945% |  |  | 2017-02-01 | 2017-03-01 | 31.5 | 0.33556 | 31.825 | 31.69 | 31.795 | 31.0425 | 31.3325 | 31.3325 | 31.8125 | 31.8125 | 0.16556 | 32.095
2016-12-01 | 27.25 | 2022 | 3.552% |  |  | 2017-03-01 | 2017-04-01 | 30 | 0.33594 | 30.325 | 30.19 | 30.295 | 29.5425 | 29.8325 | 29.8325 | 30.3125 | 30.3125 | 0.16594 | 30.595
2017-01-01 | 31.45 | 2023 | 6.201% |  |  | 2017-04-01 | 2017-05-01 | 27.75 | 0.34194 | 28.075 | 27.94 | 28.045 | 27.2925 | 27.5825 | 27.5825 | 28.0625 | 28.0625 | 0.17194 | 28.345
2017-02-01 | 31.5 | 2024 | 4.598% | Location | DA Basis vs. North Hub 10-5-2016 | 2017-05-01 | 2017-06-01 | 27.45 | 0.35086 | 27.775 | 27.64 | 27.745 | 26.9925 | 27.2825 | 27.2825 | 27.7625 | 27.7625 | 0.18086 | 28.045
2017-03-01 | 30 | 2025 | 4.797% | Aberdeen 1 | 0.325 | 2017-06-01 | 2017-07-01 | 26.45 | 0.37017 | 26.775 | 26.64 | 26.745 | 25.9925 | 26.2825 | 26.2825 | 26.7625 | 26.7625 | 0.20017 | 27.045
2017-04-01 | 27.75 | 2026 | 1.908% | Aberdeen 2 | 0.325 | 2017-07-01 | 2017-08-01 | 36.2 | 0.35684 | 36.525 | 36.39 | 36.495 | 35.7425 | 36.0325 | 36.0325 | 36.5125 | 36.5125 | 0.18684 | 36.795
2017-05-01 | 27.45 | 2027 | 0.00289% | Beethoven | 0.19 | 2017-08-01 | 2017-09-01 | 32.7 | 0.35626 | 33.025 | 32.89 | 32.995 | 32.2425 | 32.5325 | 32.5325 | 33.0125 | 33.0125 | 0.18626 | 33.295
2017-06-01 | 26.45 | 2028 | 1.056% | Big Stone | 0.295 | 2017-09-01 | 2017-10-01 | 28.8 | 0.34706 | 29.125 | 28.99 | 29.095 | 28.3425 | 28.6325 | 28.6325 | 29.1125 | 29.1125 | 0.17706 | 29.395
2017-07-01 | 36.2 | 2029 | 1.094% | Coyote | -0.4575 | 2017-10-01 | 2017-11-01 | 23.85 | 0.33307 | 24.175 | 24.04 | 24.145 | 23.3925 | 23.6825 | 23.6825 | 24.1625 | 24.1625 | 0.16307 | 24.445
2017-08-01 | 32.7 | 2030 | 1.694% | Huron 1 | -0.1675 | 2017-11-01 | 2017-12-01 | 23.8 | 0.35079 | 24.125 | 23.99 | 24.095 | 23.3425 | 23.6325 | 23.6325 | 24.1125 | 24.1125 | 0.18079 | 24.395
2017-09-01 | 28.8 | 2031 | 2.586% | Huron 2 | -0.1675 | 2017-12-01 | 2018-01-01 | 26.4 | 0.35153 | 26.725 | 26.59 | 26.695 | 25.9425 | 26.2325 | 26.2325 | 26.7125 | 26.7125 | 0.18153 | 26.995
2017-10-01 | 23.85 | 2032 | 4.517% | Neal 4 | 0.3125 | 2018-01-01 | 2018-02-01 | 35.05 | 0.34785 | 35.375 | 35.24 | 35.345 | 34.5925 | 34.8825 | 34.8825 | 35.3625 | 35.3625 | 0.17785 | 35.645
2017-11-01 | 23.8 | 2033 | 3.184% | Oak Tree | 0.3125 | 2018-02-01 | 2018-03-01 | 32.65 | 0.33349 | 32.975 | 32.84 | 32.945 | 32.1925 | 32.4825 | 32.4825 | 32.9625 | 32.9625 | 0.16349 | 33.245
2017-12-01 | 26.4 | 2034 | 3.126% | Titan | -0.17 | 2018-03-01 | 2018-04-01 | 26.9 | 0.325 | 27.225 | 27.09 | 27.195 | 26.4425 | 26.7325 | 26.7325 | 27.2125 | 27.2125 | 0.155 | 27.495
2018-01-01 | 35.05 | 2035 | 2.206% | Load | 0.27 | 2018-04-01 | 2018-05-01 | 24.45 | 0.325 | 24.775 | 24.64 | 24.745 | 23.9925 | 24.2825 | 24.2825 | 24.7625 | 24.7625 | 0.155 | 25.045
2018-02-01 | 32.65 | 2036 | 0.8074% |  |  | 2018-05-01 | 2018-06-01 | 25.3 | 0.325 | 25.625 | 25.49 | 25.595 | 24.8425 | 25.1325 | 25.1325 | 25.6125 | 25.6125 | 0.155 | 25.895
2018-03-01 | 26.9 | 2037 | 2.579% |  |  | 2018-06-01 | 2018-07-01 | 25.1 | 0.325 | 25.425 | 25.29 | 25.395 | 24.6425 | 24.9325 | 24.9325 | 25.4125 | 25.4125 | 0.155 | 25.695
2018-04-01 | 24.45 | 2038 | 2.653% |  |  | 2018-07-01 | 2018-08-01 | 31.7 | 0.325 | 32.025 | 31.89 | 31.995 | 31.2425 | 31.5325 | 31.5325 | 32.0125 | 32.0125 | 0.155 | 32.295
2018-05-01 | 25.3 | 2039 | 2.285% |  |  | 2018-08-01 | 2018-09-01 | 28.8 | 0.325 | 29.125 | 28.99 | 29.095 | 28.3425 | 28.6325 | 28.6325 | 29.1125 | 29.1125 | 0.155 | 29.395
2018-06-01 | 25.1 | 2040 | 0.849% |  |  | 2018-09-01 | 2018-10-01 | 24.25 | 0.325 | 24.575 | 24.44 | 24.545 | 23.7925 | 24.0825 | 24.0825 | 24.5625 | 24.5625 | 0.155 | 24.845
2018-07-01 | 31.7 |  |  |  |  | 2018-10-01 | 2018-11-01 | 24.4 | 0.325 | 24.725 | 24.59 | 24.695 | 23.9425 | 24.2325 | 24.2325 | 24.7125 | 24.7125 | 0.155 | 24.995
2018-08-01 | 28.8 |  |  |  |  | 2018-11-01 | 2018-12-01 | 24.3 | 0.325 | 24.625 | 24.49 | 24.595 | 23.8425 | 24.1325 | 24.1325 | 24.6125 | 24.6125 | 0.155 | 24.895
2018-09-01 | 24.25 |  |  |  |  | 2018-12-01 | 2019-01-01 | 24.8 | 0.325 | 25.125 | 24.99 | 25.095 | 24.3425 | 24.6325 | 24.6325 | 25.1125 | 25.1125 | 0.155 | 25.395
2018-10-01 | 24.4 |  |  |  |  | 2019-01-01 | 2019-02-01 | 38.3306 | 0.325 | 38.6556 | 38.5206 | 38.6256 | 37.8731 | 38.1631 | 38.1631 | 38.6431 | 38.6431 | 0.155 | 38.9256
2018-11-01 | 24.3 |  |  |  |  | 2019-02-01 | 2019-03-01 | 35.706 | 0.325 | 36.031 | 35.896 | 36.001 | 35.2485 | 35.5385 | 35.5385 | 36.0185 | 36.0185 | 0.155 | 36.301
2018-12-01 | 24.8 |  |  |  |  | 2019-03-01 | 2019-04-01 | 29.4178 | 0.325 | 29.7428 | 29.6078 | 29.7128 | 28.9603 | 29.2503 | 29.2503 | 29.7303 | 29.7303 | 0.155 | 30.0128
2019-01-01 | 38.3306 |  |  |  |  | 2019-04-01 | 2019-05-01 | 26.7385 | 0.325 | 27.0635 | 26.9285 | 27.0335 | 26.281 | 26.571 | 26.571 | 27.051 | 27.051 | 0.155 | 27.3335
2019-02-01 | 35.706 |  |  |  |  | 2019-05-01 | 2019-06-01 | 27.668 | 0.325 | 27.993 | 27.858 | 27.963 | 27.2105 | 27.5005 | 27.5005 | 27.9805 | 27.9805 | 0.155 | 28.263
2019-03-01 | 29.4178 |  |  |  |  | 2019-06-01 | 2019-07-01 | 27.4493 | 0.325 | 27.7743 | 27.6393 | 27.7443 | 26.9918 | 27.2818 | 27.2818 | 27.7618 | 27.7618 | 0.155 | 28.0443
2019-04-01 | 26.7385 |  |  |  |  | 2019-07-01 | 2019-08-01 | 34.6671 | 0.325 | 34.9921 | 34.8571 | 34.9621 | 34.2096 | 34.4996 | 34.4996 | 34.9796 | 34.9796 | 0.155 | 35.2621
2019-05-01 | 27.668 |  |  |  |  | 2019-08-01 | 2019-09-01 | 31.4956 | 0.325 | 31.8206 | 31.6856 | 31.7906 | 31.0381 | 31.3281 | 31.3281 | 31.8081 | 31.8081 | 0.155 | 32.0906
2019-06-01 | 27.4493 |  |  |  |  | 2019-09-01 | 2019-10-01 | 26.5198 | 0.325 | 26.8448 | 26.7098 | 26.8148 | 26.0623 | 26.3523 | 26.3523 | 26.8323 | 26.8323 | 0.155 | 27.1148
2019-07-01 | 34.6671 |  |  |  |  | 2019-10-01 | 2019-11-01 | 26.6838 | 0.325 | 27.0088 | 26.8738 | 26.9788 | 26.2263 | 26.5163 | 26.5163 | 26.9963 | 26.9963 | 0.155 | 27.2788
2019-08-01 | 31.4956 |  |  |  |  | 2019-11-01 | 2019-12-01 | 26.5744 | 0.325 | 26.8994 | 26.7644 | 26.8694 | 26.1169 | 26.4069 | 26.4069 | 26.8869 | 26.8869 | 0.155 | 27.1694
2019-09-01 | 26.5198 |  |  |  |  | 2019-12-01 | 2020-01-01 | 27.1212 | 0.325 | 27.4462 | 27.3112 | 27.4162 | 26.6637 | 26.9537 | 26.9537 | 27.4337 | 27.4337 | 0.155 | 27.7162
2019-10-01 | 26.6838 |  |  |  |  | 2020-01-01 | 2020-02-01 | 41.7733 | 0.325 | 42.0983 | 41.9633 | 42.0683 | 41.3158 | 41.6058 | 41.6058 | 42.0858 | 42.0858 | 0.155 | 42.3683
2019-11-01 | 26.5744 |  |  |  |  | 2020-02-01 | 2020-03-01 | 38.913 | 0.325 | 39.238 | 39.103 | 39.208 | 38.4555 | 38.7455 | 38.7455 | 39.2255 | 39.2255 | 0.155 | 39.508
2019-12-01 | 27.1212 |  |  |  |  | 2020-03-01 | 2020-04-01 | 32.06 | 0.325 | 32.385 | 32.25 | 32.355 | 31.6025 | 31.8925 | 31.8925 | 32.3725 | 32.3725 | 0.155 | 32.655
2020-01-01 | 41.7733 |  |  |  |  | 2020-04-01 | 2020-05-01 | 29.14 | 0.325 | 29.465 | 29.33 | 29.435 | 28.6825 | 28.9725 | 28.9725 | 29.4525 | 29.4525 | 0.155 | 29.735
2020-02-01 | 38.913 |  |  |  |  | 2020-05-01 | 2020-06-01 | 30.1531 | 0.325 | 30.4781 | 30.3431 | 30.4481 | 29.6956 | 29.9856 | 29.9856 | 30.4656 | 30.4656 | 0.155 | 30.7481
2020-03-01 | 32.06 |  |  |  |  | 2020-06-01 | 2020-07-01 | 29.9147 | 0.325 | 30.2397 | 30.1047 | 30.2097 | 29.4572 | 29.7472 | 29.7472 | 30.2272 | 30.2272 | 0.155 | 30.5097
2020-04-01 | 29.14 |  |  |  |  | 2020-07-01 | 2020-08-01 | 37.7807 | 0.325 | 38.1057 | 37.9707 | 38.0757 | 37.3232 | 37.6132 | 37.6132 | 38.0932 | 38.0932 | 0.155 | 38.3757
2020-05-01 | 30.1531 |  |  |  |  | 2020-08-01 | 2020-09-01 | 34.3245 | 0.325 | 34.6495 | 34.5145 | 34.6195 | 33.867 | 34.157 | 34.157 | 34.637 | 34.637 | 0.155 | 34.9195
2020-06-01 | 29.9147 |  |  |  |  | 2020-09-01 | 2020-10-01 | 28.9017 | 0.325 | 29.2267 | 29.0917 | 29.1967 | 28.4442 | 28.7342 | 28.7342 | 29.2142 | 29.2142 | 0.155 | 29.4967
2020-07-01 | 37.7807 |  |  |  |  | 2020-10-01 | 2020-11-01 | 29.0804 | 0.325 | 29.4054 | 29.2704 | 29.3754 | 28.6229 | 28.9129 | 28.9129 | 29.3929 | 29.3929 | 0.155 | 29.6754
2020-08-01 | 34.3245 |  |  |  |  | 2020-11-01 | 2020-12-01 | 28.9613 | 0.325 | 29.2863 | 29.1513 | 29.2563 | 28.5038 | 28.7938 | 28.7938 | 29.2738 | 29.2738 | 0.155 | 29.5563
2020-09-01 | 28.9017 |  |  |  |  | 2020-12-01 | 2021-01-01 | 29.5572 | 0.325 | 29.8822 | 29.7472 | 29.8522 | 29.0997 | 29.3897 | 29.3897 | 29.8697 | 29.8697 | 0.155 | 30.1522
2020-10-01 | 29.0804 |  |  |  |  | 2021-01-01 | 2021-02-01 | 43.839 | 0.325 | 44.164 | 44.029 | 44.134 | 43.3815 | 43.6715 | 43.6715 | 44.1515 | 44.1515 | 0.155 | 44.434
2020-11-01 | 28.9613 |  |  |  |  | 2021-02-01 | 2021-03-01 | 40.8372 | 0.325 | 41.1622 | 41.0272 | 41.1322 | 40.3797 | 40.6697 | 40.6697 | 41.1497 | 41.1497 | 0.155 | 41.4322
2020-12-01 | 29.5572 |  |  |  |  | 2021-03-01 | 2021-04-01 | 33.6454 | 0.325 | 33.9704 | 33.8354 | 33.9404 | 33.1879 | 33.4779 | 33.4779 | 33.9579 | 33.9579 | 0.155 | 34.2404
2021-01-01 | 43.839 |  |  |  |  | 2021-04-01 | 2021-05-01 | 30.581 | 0.325 | 30.906 | 30.771 | 30.876 | 30.1235 | 30.4135 | 30.4135 | 30.8935 | 30.8935 | 0.155 | 31.176
2021-02-01 | 40.8372 |  |  |  |  | 2021-05-01 | 2021-06-01 | 31.6442 | 0.325 | 31.9692 | 31.8342 | 31.9392 | 31.1867 | 31.4767 | 31.4767 | 31.9567 | 31.9567 | 0.155 | 32.2392
2021-03-01 | 33.6454 |  |  |  |  | 2021-06-01 | 2021-07-01 | 31.394 | 0.325 | 31.719 | 31.584 | 31.689 | 30.9365 | 31.2265 | 31.2265 | 31.7065 | 31.7065 | 0.155 | 31.989
2021-04-01 | 30.581 |  |  |  |  | 2021-07-01 | 2021-08-01 | 39.649 | 0.325 | 39.974 | 39.839 | 39.944 | 39.1915 | 39.4815 | 39.4815 | 39.9615 | 39.9615 | 0.155 | 40.244
2021-05-01 | 31.6442 |  |  |  |  | 2021-08-01 | 2021-09-01 | 36.0218 | 0.325 | 36.3468 | 36.2118 | 36.3168 | 35.5643 | 35.8543 | 35.8543 | 36.3343 | 36.3343 | 0.155 | 36.6168
2021-06-01 | 31.394 |  |  |  |  | 2021-09-01 | 2021-10-01 | 30.3309 | 0.325 | 30.6559 | 30.5209 | 30.6259 | 29.8734 | 30.1634 | 30.1634 | 30.6434 | 30.6434 | 0.155 | 30.9259
2021-07-01 | 39.649 |  |  |  |  | 2021-10-01 | 2021-11-01 | 30.5185 | 0.325 | 30.8435 | 30.7085 | 30.8135 | 30.061 | 30.351 | 30.351 | 30.831 | 30.831 | 0.155 | 31.1135
2021-08-01 | 36.0218 |  |  |  |  | 2021-11-01 | 2021-12-01 | 30.3934 | 0.325 | 30.7184 | 30.5834 | 30.6884 | 29.9359 | 30.2259 | 30.2259 | 30.7059 | 30.7059 | 0.155 | 30.9884
2021-09-01 | 30.3309 |  |  |  |  | 2021-12-01 | 2022-01-01 | 31.0188 | 0.325 | 31.3438 | 31.2088 | 31.3138 | 30.5613 | 30.8513 | 30.8513 | 31.3313 | 31.3313 | 0.155 | 31.6138
2021-10-01 | 30.5185 |  |  |  |  | 2022-01-01 | 2022-02-01 | 45.3964 | 0.325 | 45.7214 | 45.5864 | 45.6914 | 44.9389 | 45.2289 | 45.2289 | 45.7089 | 45.7089 | 0.155 | 45.9914
2021-11-01 | 30.3934 |  |  |  |  | 2022-02-01 | 2022-03-01 | 42.2879 | 0.325 | 42.6129 | 42.4779 | 42.5829 | 41.8304 | 42.1204 | 42.1204 | 42.6004 | 42.6004 | 0.155 | 42.8829
2021-12-01 | 31.0188 |  |  |  |  | 2022-03-01 | 2022-04-01 | 34.8406 | 0.325 | 35.1656 | 35.0306 | 35.1356 | 34.3831 | 34.6731 | 34.6731 | 35.1531 | 35.1531 | 0.155 | 35.4356
2022-01-01 | 45.3964 |  |  |  |  | 2022-04-01 | 2022-05-01 | 31.6674 | 0.325 | 31.9924 | 31.8574 | 31.9624 | 31.2099 | 31.4999 | 31.4999 | 31.9799 | 31.9799 | 0.155 | 32.2624
2022-02-01 | 42.2879 |  |  |  |  | 2022-05-01 | 2022-06-01 | 32.7683 | 0.325 | 33.0933 | 32.9583 | 33.0633 | 32.3108 | 32.6008 | 32.6008 | 33.0808 | 33.0808 | 0.155 | 33.3633
2022-03-01 | 34.8406 |  |  |  |  | 2022-06-01 | 2022-07-01 | 32.5093 | 0.325 | 32.8343 | 32.6993 | 32.8043 | 32.0518 | 32.3418 | 32.3418 | 32.8218 | 32.8218 | 0.155 | 33.1043
2022-04-01 | 31.6674 |  |  |  |  | 2022-07-01 | 2022-08-01 | 41.0575 | 0.325 | 41.3825 | 41.2475 | 41.3525 | 40.6 | 40.89 | 40.89 | 41.37 | 41.37 | 0.155 | 41.6525
2022-05-01 | 32.7683 |  |  |  |  | 2022-08-01 | 2022-09-01 | 37.3015 | 0.325 | 37.6265 | 37.4915 | 37.5965 | 36.844 | 37.134 | 37.134 | 37.614 | 37.614 | 0.155 | 37.8965
2022-06-01 | 32.5093 |  |  |  |  | 2022-09-01 | 2022-10-01 | 31.4084 | 0.325 | 31.7334 | 31.5984 | 31.7034 | 30.9509 | 31.2409 | 31.2409 | 31.7209 | 31.7209 | 0.155 | 32.0034
2022-07-01 | 41.0575 |  |  |  |  | 2022-10-01 | 2022-11-01 | 31.6026 | 0.325 | 31.9276 | 31.7926 | 31.8976 | 31.1451 | 31.4351 | 31.4351 | 31.9151 | 31.9151 | 0.155 | 32.1976
2022-08-01 | 37.3015 |  |  |  |  | 2022-11-01 | 2022-12-01 | 31.4731 | 0.325 | 31.7981 | 31.6631 | 31.7681 | 31.0156 | 31.3056 | 31.3056 | 31.7856 | 31.7856 | 0.155 | 32.0681
2022-09-01 | 31.4084 |  |  |  |  | 2022-12-01 | 2023-01-01 | 32.1207 | 0.325 | 32.4457 | 32.3107 | 32.4157 | 31.6632 | 31.9532 | 31.9532 | 32.4332 | 32.4332 | 0.155 | 32.7157
2022-10-01 | 31.6026 |  |  |  |  | 2023-01-01 | 2023-02-01 | 48.2113 | 0.325 | 48.5363 | 48.4013 | 48.5063 | 47.7538 | 48.0438 | 48.0438 | 48.5238 | 48.5238 | 0.155 | 48.8063
2022-11-01 | 31.4731 |  |  |  |  | 2023-02-01 | 2023-03-01 | 44.9101 | 0.325 | 45.2351 | 45.1001 | 45.2051 | 44.4526 | 44.7426 | 44.7426 | 45.2226 | 45.2226 | 0.155 | 45.5051
2022-12-01 | 32.1207 |  |  |  |  | 2023-03-01 | 2023-04-01 | 37.001 | 0.325 | 37.326 | 37.191 | 37.296 | 36.5435 | 36.8335 | 36.8335 | 37.3135 | 37.3135 | 0.155 | 37.596
2023-01-01 | 48.2113 |  |  |  |  | 2023-04-01 | 2023-05-01 | 33.631 | 0.325 | 33.956 | 33.821 | 33.926 | 33.1735 | 33.4635 | 33.4635 | 33.9435 | 33.9435 | 0.155 | 34.226
2023-02-01 | 44.9101 |  |  |  |  | 2023-05-01 | 2023-06-01 | 34.8002 | 0.325 | 35.1252 | 34.9902 | 35.0952 | 34.3427 | 34.6327 | 34.6327 | 35.1127 | 35.1127 | 0.155 | 35.3952
2023-03-01 | 37.001 |  |  |  |  | 2023-06-01 | 2023-07-01 | 34.5251 | 0.325 | 34.8501 | 34.7151 | 34.8201 | 34.0676 | 34.3576 | 34.3576 | 34.8376 | 34.8376 | 0.155 | 35.1201
2023-04-01 | 33.631 |  |  |  |  | 2023-07-01 | 2023-08-01 | 43.6034 | 0.325 | 43.9284 | 43.7934 | 43.8984 | 43.1459 | 43.4359 | 43.4359 | 43.9159 | 43.9159 | 0.155 | 44.1984
2023-05-01 | 34.8002 |  |  |  |  | 2023-08-01 | 2023-09-01 | 39.6144 | 0.325 | 39.9394 | 39.8044 | 39.9094 | 39.1569 | 39.4469 | 39.4469 | 39.9269 | 39.9269 | 0.155 | 40.2094
2023-06-01 | 34.5251 |  |  |  |  | 2023-09-01 | 2023-10-01 | 33.3559 | 0.325 | 33.6809 | 33.5459 | 33.6509 | 32.8984 | 33.1884 | 33.1884 | 33.6684 | 33.6684 | 0.155 | 33.9509
2023-07-01 | 43.6034 |  |  |  |  | 2023-10-01 | 2023-11-01 | 33.5622 | 0.325 | 33.8872 | 33.7522 | 33.8572 | 33.1047 | 33.3947 | 33.3947 | 33.8747 | 33.8747 | 0.155 | 34.1572
2023-08-01 | 39.6144 |  |  |  |  | 2023-11-01 | 2023-12-01 | 33.4247 | 0.325 | 33.7497 | 33.6147 | 33.7197 | 32.9672 | 33.2572 | 33.2572 | 33.7372 | 33.7372 | 0.155 | 34.0197
2023-09-01 | 33.3559 |  |  |  |  | 2023-12-01 | 2024-01-01 | 34.1124 | 0.325 | 34.4374 | 34.3024 | 34.4074 | 33.6549 | 33.9449 | 33.9449 | 34.4249 | 34.4249 | 0.155 | 34.7074
2023-10-01 | 33.5622 |  |  |  |  | 2024-01-01 | 2024-02-01 | 50.4282 | 0.325 | 50.7532 | 50.6182 | 50.7232 | 49.9707 | 50.2607 | 50.2607 | 50.7407 | 50.7407 | 0.155 | 51.0232
2023-11-01 | 33.4247 |  |  |  |  | 2024-02-01 | 2024-03-01 | 46.9752 | 0.325 | 47.3002 | 47.1652 | 47.2702 | 46.5177 | 46.8077 | 46.8077 | 47.2877 | 47.2877 | 0.155 | 47.5702
2023-12-01 | 34.1124 |  |  |  |  | 2024-03-01 | 2024-04-01 | 38.7024 | 0.325 | 39.0274 | 38.8924 | 38.9974 | 38.2449 | 38.5349 | 38.5349 | 39.0149 | 39.0149 | 0.155 | 39.2974
2024-01-01 | 50.4282 |  |  |  |  | 2024-04-01 | 2024-05-01 | 35.1774 | 0.325 | 35.5024 | 35.3674 | 35.4724 | 34.7199 | 35.0099 | 35.0099 | 35.4899 | 35.4899 | 0.155 | 35.7724
2024-02-01 | 46.9752 |  |  |  |  | 2024-05-01 | 2024-06-01 | 36.4004 | 0.325 | 36.7254 | 36.5904 | 36.6954 | 35.9429 | 36.2329 | 36.2329 | 36.7129 | 36.7129 | 0.155 | 36.9954
2024-03-01 | 38.7024 |  |  |  |  | 2024-06-01 | 2024-07-01 | 36.1126 | 0.325 | 36.4376 | 36.3026 | 36.4076 | 35.6551 | 35.9451 | 35.9451 | 36.4251 | 36.4251 | 0.155 | 36.7076
2024-04-01 | 35.1774 |  |  |  |  | 2024-07-01 | 2024-08-01 | 45.6084 | 0.325 | 45.9334 | 45.7984 | 45.9034 | 45.1509 | 45.4409 | 45.4409 | 45.9209 | 45.9209 | 0.155 | 46.2034
2024-05-01 | 36.4004 |  |  |  |  | 2024-08-01 | 2024-09-01 | 41.436 | 0.325 | 41.761 | 41.626 | 41.731 | 40.9785 | 41.2685 | 41.2685 | 41.7485 | 41.7485 | 0.155 | 42.031
2024-06-01 | 36.1126 |  |  |  |  | 2024-09-01 | 2024-10-01 | 34.8897 | 0.325 | 35.2147 | 35.0797 | 35.1847 | 34.4322 | 34.7222 | 34.7222 | 35.2022 | 35.2022 | 0.155 | 35.4847
2024-07-01 | 45.6084 |  |  |  |  | 2024-10-01 | 2024-11-01 | 35.1055 | 0.325 | 35.4305 | 35.2955 | 35.4005 | 34.648 | 34.938 | 34.938 | 35.418 | 35.418 | 0.155 | 35.7005
2024-08-01 | 41.436 |  |  |  |  | 2024-11-01 | 2024-12-01 | 34.9616 | 0.325 | 35.2866 | 35.1516 | 35.2566 | 34.5041 | 34.7941 | 34.7941 | 35.2741 | 35.2741 | 0.155 | 35.5566
2024-09-01 | 34.8897 |  |  |  |  | 2024-12-01 | 2025-01-01 | 35.681 | 0.325 | 36.006 | 35.871 | 35.976 | 35.2235 | 35.5135 | 35.5135 | 35.9935 | 35.9935 | 0.155 | 36.276
2024-10-01 | 35.1055 |  |  |  |  | 2025-01-01 | 2025-02-01 | 52.8473 | 0.325 | 53.1723 | 53.0373 | 53.1423 | 52.3898 | 52.6798 | 52.6798 | 53.1598 | 53.1598 | 0.155 | 53.4423
2024-11-01 | 34.9616 |  |  |  |  | 2025-02-01 | 2025-03-01 | 49.2286 | 0.325 | 49.5536 | 49.4186 | 49.5236 | 48.7711 | 49.0611 | 49.0611 | 49.5411 | 49.5411 | 0.155 | 49.8236
2024-12-01 | 35.681 |  |  |  |  | 2025-03-01 | 2025-04-01 | 40.559 | 0.325 | 40.884 | 40.749 | 40.854 | 40.1015 | 40.3915 | 40.3915 | 40.8715 | 40.8715 | 0.155 | 41.154
2025-01-01 | 52.8473 |  |  |  |  | 2025-04-01 | 2025-05-01 | 36.8649 | 0.325 | 37.1899 | 37.0549 | 37.1599 | 36.4074 | 36.6974 | 36.6974 | 37.1774 | 37.1774 | 0.155 | 37.4599
2025-02-01 | 49.2286 |  |  |  |  | 2025-05-01 | 2025-06-01 | 38.1465 | 0.325 | 38.4715 | 38.3365 | 38.4415 | 37.689 | 37.979 | 37.979 | 38.459 | 38.459 | 0.155 | 38.7415
2025-03-01 | 40.559 |  |  |  |  | 2025-06-01 | 2025-07-01 | 37.845 | 0.325 | 38.17 | 38.035 | 38.14 | 37.3875 | 37.6775 | 37.6775 | 38.1575 | 38.1575 | 0.155 | 38.44
2025-04-01 | 36.8649 |  |  |  |  | 2025-07-01 | 2025-08-01 | 47.7963 | 0.325 | 48.1213 | 47.9863 | 48.0913 | 47.3388 | 47.6288 | 47.6288 | 48.1088 | 48.1088 | 0.155 | 48.3913
2025-05-01 | 38.1465 |  |  |  |  | 2025-08-01 | 2025-09-01 | 43.4237 | 0.325 | 43.7487 | 43.6137 | 43.7187 | 42.9662 | 43.2562 | 43.2562 | 43.7362 | 43.7362 | 0.155 | 44.0187
2025-06-01 | 37.845 |  |  |  |  | 2025-09-01 | 2025-10-01 | 36.5634 | 0.325 | 36.8884 | 36.7534 | 36.8584 | 36.1059 | 36.3959 | 36.3959 | 36.8759 | 36.8759 | 0.155 | 37.1584
2025-07-01 | 47.7963 |  |  |  |  | 2025-10-01 | 2025-11-01 | 36.7896 | 0.325 | 37.1146 | 36.9796 | 37.0846 | 36.3321 | 36.6221 | 36.6221 | 37.1021 | 37.1021 | 0.155 | 37.3846
2025-08-01 | 43.4237 |  |  |  |  | 2025-11-01 | 2025-12-01 | 36.6388 | 0.325 | 36.9638 | 36.8288 | 36.9338 | 36.1813 | 36.4713 | 36.4713 | 36.9513 | 36.9513 | 0.155 | 37.2338
2025-09-01 | 36.5634 |  |  |  |  | 2025-12-01 | 2026-01-01 | 37.3927 | 0.325 | 37.7177 | 37.5827 | 37.6877 | 36.9352 | 37.2252 | 37.2252 | 37.7052 | 37.7052 | 0.155 | 37.9877
2025-10-01 | 36.7896 |  |  |  |  | 2026-01-01 | 2026-02-01 | 53.8558 | 0.325 | 54.1808 | 54.0458 | 54.1508 | 53.3983 | 53.6883 | 53.6883 | 54.1683 | 54.1683 | 0.155 | 54.4508
2025-11-01 | 36.6388 |  |  |  |  | 2026-02-01 | 2026-03-01 | 50.1681 | 0.325 | 50.4931 | 50.3581 | 50.4631 | 49.7106 | 50.0006 | 50.0006 | 50.4806 | 50.4806 | 0.155 | 50.7631
2025-12-01 | 37.3927 |  |  |  |  | 2026-03-01 | 2026-04-01 | 41.333 | 0.325 | 41.658 | 41.523 | 41.628 | 40.8755 | 41.1655 | 41.1655 | 41.6455 | 41.6455 | 0.155 | 41.928
2026-01-01 | 53.8558 |  |  |  |  | 2026-04-01 | 2026-05-01 | 37.5685 | 0.325 | 37.8935 | 37.7585 | 37.8635 | 37.111 | 37.401 | 37.401 | 37.881 | 37.881 | 0.155 | 38.1635
2026-02-01 | 50.1681 |  |  |  |  | 2026-05-01 | 2026-06-01 | 38.8745 | 0.325 | 39.1995 | 39.0645 | 39.1695 | 38.417 | 38.707 | 38.707 | 39.187 | 39.187 | 0.155 | 39.4695
2026-03-01 | 41.333 |  |  |  |  | 2026-06-01 | 2026-07-01 | 38.5672 | 0.325 | 38.8922 | 38.7572 | 38.8622 | 38.1097 | 38.3997 | 38.3997 | 38.8797 | 38.8797 | 0.155 | 39.1622
2026-04-01 | 37.5685 |  |  |  |  | 2026-07-01 | 2026-08-01 | 48.7084 | 0.325 | 49.0334 | 48.8984 | 49.0034 | 48.2509 | 48.5409 | 48.5409 | 49.0209 | 49.0209 | 0.155 | 49.3034
2026-05-01 | 38.8745 |  |  |  |  | 2026-08-01 | 2026-09-01 | 44.2524 | 0.325 | 44.5774 | 44.4424 | 44.5474 | 43.7949 | 44.0849 | 44.0849 | 44.5649 | 44.5649 | 0.155 | 44.8474
2026-06-01 | 38.5672 |  |  |  |  | 2026-09-01 | 2026-10-01 | 37.2612 | 0.325 | 37.5862 | 37.4512 | 37.5562 | 36.8037 | 37.0937 | 37.0937 | 37.5737 | 37.5737 | 0.155 | 37.8562
2026-07-01 | 48.7084 |  |  |  |  | 2026-10-01 | 2026-11-01 | 37.4916 | 0.325 | 37.8166 | 37.6816 | 37.7866 | 37.0341 | 37.3241 | 37.3241 | 37.8041 | 37.8041 | 0.155 | 38.0866
2026-08-01 | 44.2524 |  |  |  |  | 2026-11-01 | 2026-12-01 | 37.338 | 0.325 | 37.663 | 37.528 | 37.633 | 36.8805 | 37.1705 | 37.1705 | 37.6505 | 37.6505 | 0.155 | 37.933
2026-09-01 | 37.2612 |  |  |  |  | 2026-12-01 | 2027-01-01 | 38.1063 | 0.325 | 38.4313 | 38.2963 | 38.4013 | 37.6488 | 37.9388 | 37.9388 | 38.4188 | 38.4188 | 0.155 | 38.7013
2026-10-01 | 37.4916 |  |  |  |  | 2027-01-01 | 2027-02-01 | 53.8574 | 0.325 | 54.1824 | 54.0474 | 54.1524 | 53.3999 | 53.6899 | 53.6899 | 54.1699 | 54.1699 | 0.155 | 54.4524
2026-11-01 | 37.338 |  |  |  |  | 2027-02-01 | 2027-03-01 | 50.1696 | 0.325 | 50.4946 | 50.3596 | 50.4646 | 49.7121 | 50.0021 | 50.0021 | 50.4821 | 50.4821 | 0.155 | 50.7646
2026-12-01 | 38.1063 |  |  |  |  | 2027-03-01 | 2027-04-01 | 41.3342 | 0.325 | 41.6592 | 41.5242 | 41.6292 | 40.8767 | 41.1667 | 41.1667 | 41.6467 | 41.6467 | 0.155 | 41.9292
2027-01-01 | 53.8574 |  |  |  |  | 2027-04-01 | 2027-05-01 | 37.5696 | 0.325 | 37.8946 | 37.7596 | 37.8646 | 37.1121 | 37.4021 | 37.4021 | 37.8821 | 37.8821 | 0.155 | 38.1646
2027-02-01 | 50.1696 |  |  |  |  | 2027-05-01 | 2027-06-01 | 38.8757 | 0.325 | 39.2007 | 39.0657 | 39.1707 | 38.4182 | 38.7082 | 38.7082 | 39.1882 | 39.1882 | 0.155 | 39.4707
2027-03-01 | 41.3342 |  |  |  |  | 2027-06-01 | 2027-07-01 | 38.5683 | 0.325 | 38.8933 | 38.7583 | 38.8633 | 38.1108 | 38.4008 | 38.4008 | 38.8808 | 38.8808 | 0.155 | 39.1633
2027-04-01 | 37.5696 |  |  |  |  | 2027-07-01 | 2027-08-01 | 48.7098 | 0.325 | 49.0348 | 48.8998 | 49.0048 | 48.2523 | 48.5423 | 48.5423 | 49.0223 | 49.0223 | 0.155 | 49.3048
2027-05-01 | 38.8757 |  |  |  |  | 2027-08-01 | 2027-09-01 | 44.2537 | 0.325 | 44.5787 | 44.4437 | 44.5487 | 43.7962 | 44.0862 | 44.0862 | 44.5662 | 44.5662 | 0.155 | 44.8487
2027-06-01 | 38.5683 |  |  |  |  | 2027-09-01 | 2027-10-01 | 37.2622 | 0.325 | 37.5872 | 37.4522 | 37.5572 | 36.8047 | 37.0947 | 37.0947 | 37.5747 | 37.5747 | 0.155 | 37.8572
2027-07-01 | 48.7098 |  |  |  |  | 2027-10-01 | 2027-11-01 | 37.4927 | 0.325 | 37.8177 | 37.6827 | 37.7877 | 37.0352 | 37.3252 | 37.3252 | 37.8052 | 37.8052 | 0.155 | 38.0877
2027-08-01 | 44.2537 |  |  |  |  | 2027-11-01 | 2027-12-01 | 37.3391 | 0.325 | 37.6641 | 37.5291 | 37.6341 | 36.8816 | 37.1716 | 37.1716 | 37.6516 | 37.6516 | 0.155 | 37.9341
2027-09-01 | 37.2622 |  |  |  |  | 2027-12-01 | 2028-01-01 | 38.1074 | 0.325 | 38.4324 | 38.2974 | 38.4024 | 37.6499 | 37.9399 | 37.9399 | 38.4199 | 38.4199 | 0.155 | 38.7024
2027-10-01 | 37.4927 |  |  |  |  | 2028-01-01 | 2028-02-01 | 54.4261 | 0.325 | 54.7511 | 54.6161 | 54.7211 | 53.9686 | 54.2586 | 54.2586 | 54.7386 | 54.7386 | 0.155 | 55.0211
2027-11-01 | 37.3391 |  |  |  |  | 2028-02-01 | 2028-03-01 | 50.6993 | 0.325 | 51.0243 | 50.8893 | 50.9943 | 50.2418 | 50.5318 | 50.5318 | 51.0118 | 51.0118 | 0.155 | 51.2943
2027-12-01 | 38.1074 |  |  |  |  | 2028-03-01 | 2028-04-01 | 41.7707 | 0.325 | 42.0957 | 41.9607 | 42.0657 | 41.3132 | 41.6032 | 41.6032 | 42.0832 | 42.0832 | 0.155 | 42.3657
2028-01-01 | 54.4261 |  |  |  |  | 2028-04-01 | 2028-05-01 | 37.9663 | 0.325 | 38.2913 | 38.1563 | 38.2613 | 37.5088 | 37.7988 | 37.7988 | 38.2788 | 38.2788 | 0.155 | 38.5613
2028-02-01 | 50.6993 |  |  |  |  | 2028-05-01 | 2028-06-01 | 39.2862 | 0.325 | 39.6112 | 39.4762 | 39.5812 | 38.8287 | 39.1187 | 39.1187 | 39.5987 | 39.5987 | 0.155 | 39.8812
2028-03-01 | 41.7707 |  |  |  |  | 2028-06-01 | 2028-07-01 | 38.9756 | 0.325 | 39.3006 | 39.1656 | 39.2706 | 38.5181 | 38.8081 | 38.8081 | 39.2881 | 39.2881 | 0.155 | 39.5706
2028-04-01 | 37.9663 |  |  |  |  | 2028-07-01 | 2028-08-01 | 49.2242 | 0.325 | 49.5492 | 49.4142 | 49.5192 | 48.7667 | 49.0567 | 49.0567 | 49.5367 | 49.5367 | 0.155 | 49.8192
2028-05-01 | 39.2862 |  |  |  |  | 2028-08-01 | 2028-09-01 | 44.721 | 0.325 | 45.046 | 44.911 | 45.016 | 44.2635 | 44.5535 | 44.5535 | 45.0335 | 45.0335 | 0.155 | 45.316
2028-06-01 | 38.9756 |  |  |  |  | 2028-09-01 | 2028-10-01 | 37.6557 | 0.325 | 37.9807 | 37.8457 | 37.9507 | 37.1982 | 37.4882 | 37.4882 | 37.9682 | 37.9682 | 0.155 | 38.2507
2028-07-01 | 49.2242 |  |  |  |  | 2028-10-01 | 2028-11-01 | 37.8886 | 0.325 | 38.2136 | 38.0786 | 38.1836 | 37.4311 | 37.7211 | 37.7211 | 38.2011 | 38.2011 | 0.155 | 38.4836
2028-08-01 | 44.721 |  |  |  |  | 2028-11-01 | 2028-12-01 | 37.7333 | 0.325 | 38.0583 | 37.9233 | 38.0283 | 37.2758 | 37.5658 | 37.5658 | 38.0458 | 38.0458 | 0.155 | 38.3283
2028-09-01 | 37.6557 |  |  |  |  | 2028-12-01 | 2029-01-01 | 38.5097 | 0.325 | 38.8347 | 38.6997 | 38.8047 | 38.0522 | 38.3422 | 38.3422 | 38.8222 | 38.8222 | 0.155 | 39.1047
2028-10-01 | 37.8886 |  |  |  |  | 2029-01-01 | 2029-02-01 | 55.0213 | 0.325 | 55.3463 | 55.2113 | 55.3163 | 54.5638 | 54.8538 | 54.8538 | 55.3338 | 55.3338 | 0.155 | 55.6163
2028-11-01 | 37.7333 |  |  |  |  | 2029-02-01 | 2029-03-01 | 51.2538 | 0.325 | 51.5788 | 51.4438 | 51.5488 | 50.7963 | 51.0863 | 51.0863 | 51.5663 | 51.5663 | 0.155 | 51.8488
2028-12-01 | 38.5097 |  |  |  |  | 2029-03-01 | 2029-04-01 | 42.2275 | 0.325 | 42.5525 | 42.4175 | 42.5225 | 41.77 | 42.06 | 42.06 | 42.54 | 42.54 | 0.155 | 42.8225
2029-01-01 | 55.0213 |  |  |  |  | 2029-04-01 | 2029-05-01 | 38.3815 | 0.325 | 38.7065 | 38.5715 | 38.6765 | 37.924 | 38.214 | 38.214 | 38.694 | 38.694 | 0.155 | 38.9765
2029-02-01 | 51.2538 |  |  |  |  | 2029-05-01 | 2029-06-01 | 39.7158 | 0.325 | 40.0408 | 39.9058 | 40.0108 | 39.2583 | 39.5483 | 39.5483 | 40.0283 | 40.0283 | 0.155 | 40.3108
2029-03-01 | 42.2275 |  |  |  |  | 2029-06-01 | 2029-07-01 | 39.4019 | 0.325 | 39.7269 | 39.5919 | 39.6969 | 38.9444 | 39.2344 | 39.2344 | 39.7144 | 39.7144 | 0.155 | 39.9969
2029-04-01 | 38.3815 |  |  |  |  | 2029-07-01 | 2029-08-01 | 49.7625 | 0.325 | 50.0875 | 49.9525 | 50.0575 | 49.305 | 49.595 | 49.595 | 50.075 | 50.075 | 0.155 | 50.3575
2029-05-01 | 39.7158 |  |  |  |  | 2029-08-01 | 2029-09-01 | 45.2101 | 0.325 | 45.5351 | 45.4001 | 45.5051 | 44.7526 | 45.0426 | 45.0426 | 45.5226 | 45.5226 | 0.155 | 45.8051
2029-06-01 | 39.4019 |  |  |  |  | 2029-09-01 | 2029-10-01 | 38.0676 | 0.325 | 38.3926 | 38.2576 | 38.3626 | 37.6101 | 37.9001 | 37.9001 | 38.3801 | 38.3801 | 0.155 | 38.6626
2029-07-01 | 49.7625 |  |  |  |  | 2029-10-01 | 2029-11-01 | 38.303 | 0.325 | 38.628 | 38.493 | 38.598 | 37.8455 | 38.1355 | 38.1355 | 38.6155 | 38.6155 | 0.155 | 38.898
2029-08-01 | 45.2101 |  |  |  |  | 2029-11-01 | 2029-12-01 | 38.146 | 0.325 | 38.471 | 38.336 | 38.441 | 37.6885 | 37.9785 | 37.9785 | 38.4585 | 38.4585 | 0.155 | 38.741
2029-09-01 | 38.0676 |  |  |  |  | 2029-12-01 | 2030-01-01 | 38.9309 | 0.325 | 39.2559 | 39.1209 | 39.2259 | 38.4734 | 38.7634 | 38.7634 | 39.2434 | 39.2434 | 0.155 | 39.5259
2029-10-01 | 38.303 |  |  |  |  | 2030-01-01 | 2030-02-01 | 55.9537 | 0.325 | 56.2787 | 56.1437 | 56.2487 | 55.4962 | 55.7862 | 55.7862 | 56.2662 | 56.2662 | 0.155 | 56.5487
2029-11-01 | 38.146 |  |  |  |  | 2030-02-01 | 2030-03-01 | 52.1223 | 0.325 | 52.4473 | 52.3123 | 52.4173 | 51.6648 | 51.9548 | 51.9548 | 52.4348 | 52.4348 | 0.155 | 52.7173
2029-12-01 | 38.9309 |  |  |  |  | 2030-03-01 | 2030-04-01 | 42.943 | 0.325 | 43.268 | 43.133 | 43.238 | 42.4855 | 42.7755 | 42.7755 | 43.2555 | 43.2555 | 0.155 | 43.538
2030-01-01 | 55.9537 |  |  |  |  | 2030-04-01 | 2030-05-01 | 39.0319 | 0.325 | 39.3569 | 39.2219 | 39.3269 | 38.5744 | 38.8644 | 38.8644 | 39.3444 | 39.3444 | 0.155 | 39.6269
2030-02-01 | 52.1223 |  |  |  |  | 2030-05-01 | 2030-06-01 | 40.3888 | 0.325 | 40.7138 | 40.5788 | 40.6838 | 39.9313 | 40.2213 | 40.2213 | 40.7013 | 40.7013 | 0.155 | 40.9838
2030-03-01 | 42.943 |  |  |  |  | 2030-06-01 | 2030-07-01 | 40.0695 | 0.325 | 40.3945 | 40.2595 | 40.3645 | 39.612 | 39.902 | 39.902 | 40.382 | 40.382 | 0.155 | 40.6645
2030-04-01 | 39.0319 |  |  |  |  | 2030-07-01 | 2030-08-01 | 50.6057 | 0.325 | 50.9307 | 50.7957 | 50.9007 | 50.1482 | 50.4382 | 50.4382 | 50.9182 | 50.9182 | 0.155 | 51.2007
2030-05-01 | 40.3888 |  |  |  |  | 2030-08-01 | 2030-09-01 | 45.9762 | 0.325 | 46.3012 | 46.1662 | 46.2712 | 45.5187 | 45.8087 | 45.8087 | 46.2887 | 46.2887 | 0.155 | 46.5712
2030-06-01 | 40.0695 |  |  |  |  | 2030-09-01 | 2030-10-01 | 38.7126 | 0.325 | 39.0376 | 38.9026 | 39.0076 | 38.2551 | 38.5451 | 38.5451 | 39.0251 | 39.0251 | 0.155 | 39.3076
2030-07-01 | 50.6057 |  |  |  |  | 2030-10-01 | 2030-11-01 | 38.952 | 0.325 | 39.277 | 39.142 | 39.247 | 38.4945 | 38.7845 | 38.7845 | 39.2645 | 39.2645 | 0.155 | 39.547
2030-08-01 | 45.9762 |  |  |  |  | 2030-11-01 | 2030-12-01 | 38.7924 | 0.325 | 39.1174 | 38.9824 | 39.0874 | 38.3349 | 38.6249 | 38.6249 | 39.1049 | 39.1049 | 0.155 | 39.3874
2030-09-01 | 38.7126 |  |  |  |  | 2030-12-01 | 2031-01-01 | 39.5906 | 0.325 | 39.9156 | 39.7806 | 39.8856 | 39.1331 | 39.4231 | 39.4231 | 39.9031 | 39.9031 | 0.155 | 40.1856
2030-10-01 | 38.952 |  |  |  |  | 2031-01-01 | 2031-02-01 | 57.4008 | 0.325 | 57.7258 | 57.5908 | 57.6958 | 56.9433 | 57.2333 | 57.2333 | 57.7133 | 57.7133 | 0.155 | 57.9958
2030-11-01 | 38.7924 |  |  |  |  | 2031-02-01 | 2031-03-01 | 53.4704 | 0.325 | 53.7954 | 53.6604 | 53.7654 | 53.0129 | 53.3029 | 53.3029 | 53.7829 | 53.7829 | 0.155 | 54.0654
2030-12-01 | 39.5906 |  |  |  |  | 2031-03-01 | 2031-04-01 | 44.0537 | 0.325 | 44.3787 | 44.2437 | 44.3487 | 43.5962 | 43.8862 | 43.8862 | 44.3662 | 44.3662 | 0.155 | 44.6487
2031-01-01 | 57.4008 |  |  |  |  | 2031-04-01 | 2031-05-01 | 40.0414 | 0.325 | 40.3664 | 40.2314 | 40.3364 | 39.5839 | 39.8739 | 39.8739 | 40.3539 | 40.3539 | 0.155 | 40.6364
2031-02-01 | 53.4704 |  |  |  |  | 2031-05-01 | 2031-06-01 | 41.4334 | 0.325 | 41.7584 | 41.6234 | 41.7284 | 40.9759 | 41.2659 | 41.2659 | 41.7459 | 41.7459 | 0.155 | 42.0284
2031-03-01 | 44.0537 |  |  |  |  | 2031-06-01 | 2031-07-01 | 41.1059 | 0.325 | 41.4309 | 41.2959 | 41.4009 | 40.6484 | 40.9384 | 40.9384 | 41.4184 | 41.4184 | 0.155 | 41.7009
2031-04-01 | 40.0414 |  |  |  |  | 2031-07-01 | 2031-08-01 | 51.9146 | 0.325 | 52.2396 | 52.1046 | 52.2096 | 51.4571 | 51.7471 | 51.7471 | 52.2271 | 52.2271 | 0.155 | 52.5096
2031-05-01 | 41.4334 |  |  |  |  | 2031-08-01 | 2031-09-01 | 47.1653 | 0.325 | 47.4903 | 47.3553 | 47.4603 | 46.7078 | 46.9978 | 46.9978 | 47.4778 | 47.4778 | 0.155 | 47.7603
2031-06-01 | 41.1059 |  |  |  |  | 2031-09-01 | 2031-10-01 | 39.7138 | 0.325 | 40.0388 | 39.9038 | 40.0088 | 39.2563 | 39.5463 | 39.5463 | 40.0263 | 40.0263 | 0.155 | 40.3088
2031-07-01 | 51.9146 |  |  |  |  | 2031-10-01 | 2031-11-01 | 39.9595 | 0.325 | 40.2845 | 40.1495 | 40.2545 | 39.502 | 39.792 | 39.792 | 40.272 | 40.272 | 0.155 | 40.5545
2031-08-01 | 47.1653 |  |  |  |  | 2031-11-01 | 2031-12-01 | 39.7957 | 0.325 | 40.1207 | 39.9857 | 40.0907 | 39.3382 | 39.6282 | 39.6282 | 40.1082 | 40.1082 | 0.155 | 40.3907
2031-09-01 | 39.7138 |  |  |  |  | 2031-12-01 | 2032-01-01 | 40.6146 | 0.325 | 40.9396 | 40.8046 | 40.9096 | 40.1571 | 40.4471 | 40.4471 | 40.9271 | 40.9271 | 0.155 | 41.2096
2031-10-01 | 39.9595 |  |  |  |  | 2032-01-01 | 2032-02-01 | 59.9935 | 0.325 | 60.3185 | 60.1835 | 60.2885 | 59.536 | 59.826 | 59.826 | 60.306 | 60.306 | 0.155 | 60.5885
2031-11-01 | 39.7957 |  |  |  |  | 2032-02-01 | 2032-03-01 | 55.8855 | 0.325 | 56.2105 | 56.0755 | 56.1805 | 55.428 | 55.718 | 55.718 | 56.198 | 56.198 | 0.155 | 56.4805
2031-12-01 | 40.6146 |  |  |  |  | 2032-03-01 | 2032-04-01 | 46.0435 | 0.325 | 46.3685 | 46.2335 | 46.3385 | 45.586 | 45.876 | 45.876 | 46.356 | 46.356 | 0.155 | 46.6385
2032-01-01 | 59.9935 |  |  |  |  | 2032-04-01 | 2032-05-01 | 41.8499 | 0.325 | 42.1749 | 42.0399 | 42.1449 | 41.3924 | 41.6824 | 41.6824 | 42.1624 | 42.1624 | 0.155 | 42.4449
2032-02-01 | 55.8855 |  |  |  |  | 2032-05-01 | 2032-06-01 | 43.3048 | 0.325 | 43.6298 | 43.4948 | 43.5998 | 42.8473 | 43.1373 | 43.1373 | 43.6173 | 43.6173 | 0.155 | 43.8998
2032-03-01 | 46.0435 |  |  |  |  | 2032-06-01 | 2032-07-01 | 42.9625 | 0.325 | 43.2875 | 43.1525 | 43.2575 | 42.505 | 42.795 | 42.795 | 43.275 | 43.275 | 0.155 | 43.5575
2032-04-01 | 41.8499 |  |  |  |  | 2032-07-01 | 2032-08-01 | 54.2594 | 0.325 | 54.5844 | 54.4494 | 54.5544 | 53.8019 | 54.0919 | 54.0919 | 54.5719 | 54.5719 | 0.155 | 54.8544
2032-05-01 | 43.3048 |  |  |  |  | 2032-08-01 | 2032-09-01 | 49.2956 | 0.325 | 49.6206 | 49.4856 | 49.5906 | 48.8381 | 49.1281 | 49.1281 | 49.6081 | 49.6081 | 0.155 | 49.8906
2032-06-01 | 42.9625 |  |  |  |  | 2032-09-01 | 2032-10-01 | 41.5076 | 0.325 | 41.8326 | 41.6976 | 41.8026 | 41.0501 | 41.3401 | 41.3401 | 41.8201 | 41.8201 | 0.155 | 42.1026
2032-07-01 | 54.2594 |  |  |  |  | 2032-10-01 | 2032-11-01 | 41.7644 | 0.325 | 42.0894 | 41.9544 | 42.0594 | 41.3069 | 41.5969 | 41.5969 | 42.0769 | 42.0769 | 0.155 | 42.3594
2032-08-01 | 49.2956 |  |  |  |  | 2032-11-01 | 2032-12-01 | 41.5932 | 0.325 | 41.9182 | 41.7832 | 41.8882 | 41.1357 | 41.4257 | 41.4257 | 41.9057 | 41.9057 | 0.155 | 42.1882
2032-09-01 | 41.5076 |  |  |  |  | 2032-12-01 | 2033-01-01 | 42.449 | 0.325 | 42.774 | 42.639 | 42.744 | 41.9915 | 42.2815 | 42.2815 | 42.7615 | 42.7615 | 0.155 | 43.044
2032-10-01 | 41.7644 |  |  |  |  | 2033-01-01 | 2033-02-01 | 61.9034 | 0.325 | 62.2284 | 62.0934 | 62.1984 | 61.4459 | 61.7359 | 61.7359 | 62.2159 | 62.2159 | 0.155 | 62.4984
2032-11-01 | 41.5932 |  |  |  |  | 2033-02-01 | 2033-03-01 | 57.6647 | 0.325 | 57.9897 | 57.8547 | 57.9597 | 57.2072 | 57.4972 | 57.4972 | 57.9772 | 57.9772 | 0.155 | 58.2597
2032-12-01 | 42.449 |  |  |  |  | 2033-03-01 | 2033-04-01 | 47.5093 | 0.325 | 47.8343 | 47.6993 | 47.8043 | 47.0518 | 47.3418 | 47.3418 | 47.8218 | 47.8218 | 0.155 | 48.1043
2033-01-01 | 61.9034 |  |  |  |  | 2033-04-01 | 2033-05-01 | 43.1823 | 0.325 | 43.5073 | 43.3723 | 43.4773 | 42.7248 | 43.0148 | 43.0148 | 43.4948 | 43.4948 | 0.155 | 43.7773
2033-02-01 | 57.6647 |  |  |  |  | 2033-05-01 | 2033-06-01 | 44.6835 | 0.325 | 45.0085 | 44.8735 | 44.9785 | 44.226 | 44.516 | 44.516 | 44.996 | 44.996 | 0.155 | 45.2785
2033-03-01 | 47.5093 |  |  |  |  | 2033-06-01 | 2033-07-01 | 44.3303 | 0.325 | 44.6553 | 44.5203 | 44.6253 | 43.8728 | 44.1628 | 44.1628 | 44.6428 | 44.6428 | 0.155 | 44.9253
2033-04-01 | 43.1823 |  |  |  |  | 2033-07-01 | 2033-08-01 | 55.9868 | 0.325 | 56.3118 | 56.1768 | 56.2818 | 55.5293 | 55.8193 | 55.8193 | 56.2993 | 56.2993 | 0.155 | 56.5818
2033-05-01 | 44.6835 |  |  |  |  | 2033-08-01 | 2033-09-01 | 50.865 | 0.325 | 51.19 | 51.055 | 51.16 | 50.4075 | 50.6975 | 50.6975 | 51.1775 | 51.1775 | 0.155 | 51.46
2033-06-01 | 44.3303 |  |  |  |  | 2033-09-01 | 2033-10-01 | 42.829 | 0.325 | 43.154 | 43.019 | 43.124 | 42.3715 | 42.6615 | 42.6615 | 43.1415 | 43.1415 | 0.155 | 43.424
2033-07-01 | 55.9868 |  |  |  |  | 2033-10-01 | 2033-11-01 | 43.094 | 0.325 | 43.419 | 43.284 | 43.389 | 42.6365 | 42.9265 | 42.9265 | 43.4065 | 43.4065 | 0.155 | 43.689
2033-08-01 | 50.865 |  |  |  |  | 2033-11-01 | 2033-12-01 | 42.9174 | 0.325 | 43.2424 | 43.1074 | 43.2124 | 42.4599 | 42.7499 | 42.7499 | 43.2299 | 43.2299 | 0.155 | 43.5124
2033-09-01 | 42.829 |  |  |  |  | 2033-12-01 | 2034-01-01 | 43.8004 | 0.325 | 44.1254 | 43.9904 | 44.0954 | 43.3429 | 43.6329 | 43.6329 | 44.1129 | 44.1129 | 0.155 | 44.3954
2033-10-01 | 43.094 |  |  |  |  | 2034-01-01 | 2034-02-01 | 63.8384 | 0.325 | 64.1634 | 64.0284 | 64.1334 | 63.3809 | 63.6709 | 63.6709 | 64.1509 | 64.1509 | 0.155 | 64.4334
2033-11-01 | 42.9174 |  |  |  |  | 2034-02-01 | 2034-03-01 | 59.4671 | 0.325 | 59.7921 | 59.6571 | 59.7621 | 59.0096 | 59.2996 | 59.2996 | 59.7796 | 59.7796 | 0.155 | 60.0621
2033-12-01 | 43.8004 |  |  |  |  | 2034-03-01 | 2034-04-01 | 48.9943 | 0.325 | 49.3193 | 49.1843 | 49.2893 | 48.5368 | 48.8268 | 48.8268 | 49.3068 | 49.3068 | 0.155 | 49.5893
2034-01-01 | 63.8384 |  |  |  |  | 2034-04-01 | 2034-05-01 | 44.532 | 0.325 | 44.857 | 44.722 | 44.827 | 44.0745 | 44.3645 | 44.3645 | 44.8445 | 44.8445 | 0.155 | 45.127
2034-02-01 | 59.4671 |  |  |  |  | 2034-05-01 | 2034-06-01 | 46.0802 | 0.325 | 46.4052 | 46.2702 | 46.3752 | 45.6227 | 45.9127 | 45.9127 | 46.3927 | 46.3927 | 0.155 | 46.6752
2034-03-01 | 48.9943 |  |  |  |  | 2034-06-01 | 2034-07-01 | 45.7159 | 0.325 | 46.0409 | 45.9059 | 46.0109 | 45.2584 | 45.5484 | 45.5484 | 46.0284 | 46.0284 | 0.155 | 46.3109
2034-04-01 | 44.532 |  |  |  |  | 2034-07-01 | 2034-08-01 | 57.7368 | 0.325 | 58.0618 | 57.9268 | 58.0318 | 57.2793 | 57.5693 | 57.5693 | 58.0493 | 58.0493 | 0.155 | 58.3318
2034-05-01 | 46.0802 |  |  |  |  | 2034-08-01 | 2034-09-01 | 52.4549 | 0.325 | 52.7799 | 52.6449 | 52.7499 | 51.9974 | 52.2874 | 52.2874 | 52.7674 | 52.7674 | 0.155 | 53.0499
2034-06-01 | 45.7159 |  |  |  |  | 2034-09-01 | 2034-10-01 | 44.1678 | 0.325 | 44.4928 | 44.3578 | 44.4628 | 43.7103 | 44.0003 | 44.0003 | 44.4803 | 44.4803 | 0.155 | 44.7628
2034-07-01 | 57.7368 |  |  |  |  | 2034-10-01 | 2034-11-01 | 44.441 | 0.325 | 44.766 | 44.631 | 44.736 | 43.9835 | 44.2735 | 44.2735 | 44.7535 | 44.7535 | 0.155 | 45.036
2034-08-01 | 52.4549 |  |  |  |  | 2034-11-01 | 2034-12-01 | 44.2588 | 0.325 | 44.5838 | 44.4488 | 44.5538 | 43.8013 | 44.0913 | 44.0913 | 44.5713 | 44.5713 | 0.155 | 44.8538
2034-09-01 | 44.1678 |  |  |  |  | 2034-12-01 | 2035-01-01 | 45.1695 | 0.325 | 45.4945 | 45.3595 | 45.4645 | 44.712 | 45.002 | 45.002 | 45.482 | 45.482 | 0.155 | 45.7645
2034-10-01 | 44.441 |  |  |  |  | 2035-01-01 | 2035-02-01 | 65.2469 | 0.325 | 65.5719 | 65.4369 | 65.5419 | 64.7894 | 65.0794 | 65.0794 | 65.5594 | 65.5594 | 0.155 | 65.8419
2034-11-01 | 44.2588 |  |  |  |  | 2035-02-01 | 2035-03-01 | 60.7792 | 0.325 | 61.1042 | 60.9692 | 61.0742 | 60.3217 | 60.6117 | 60.6117 | 61.0917 | 61.0917 | 0.155 | 61.3742
2034-12-01 | 45.1695 |  |  |  |  | 2035-03-01 | 2035-04-01 | 50.0754 | 0.325 | 50.4004 | 50.2654 | 50.3704 | 49.6179 | 49.9079 | 49.9079 | 50.3879 | 50.3879 | 0.155 | 50.6704
2035-01-01 | 65.2469 |  |  |  |  | 2035-04-01 | 2035-05-01 | 45.5146 | 0.325 | 45.8396 | 45.7046 | 45.8096 | 45.0571 | 45.3471 | 45.3471 | 45.8271 | 45.8271 | 0.155 | 46.1096
2035-02-01 | 60.7792 |  |  |  |  | 2035-05-01 | 2035-06-01 | 47.0969 | 0.325 | 47.4219 | 47.2869 | 47.3919 | 46.6394 | 46.9294 | 46.9294 | 47.4094 | 47.4094 | 0.155 | 47.6919
2035-03-01 | 50.0754 |  |  |  |  | 2035-06-01 | 2035-07-01 | 46.7246 | 0.325 | 47.0496 | 46.9146 | 47.0196 | 46.2671 | 46.5571 | 46.5571 | 47.0371 | 47.0371 | 0.155 | 47.3196
2035-04-01 | 45.5146 |  |  |  |  | 2035-07-01 | 2035-08-01 | 59.0107 | 0.325 | 59.3357 | 59.2007 | 59.3057 | 58.5532 | 58.8432 | 58.8432 | 59.3232 | 59.3232 | 0.155 | 59.6057
2035-05-01 | 47.0969 |  |  |  |  | 2035-08-01 | 2035-09-01 | 53.6123 | 0.325 | 53.9373 | 53.8023 | 53.9073 | 53.1548 | 53.4448 | 53.4448 | 53.9248 | 53.9248 | 0.155 | 54.2073
2035-06-01 | 46.7246 |  |  |  |  | 2035-09-01 | 2035-10-01 | 45.1423 | 0.325 | 45.4673 | 45.3323 | 45.4373 | 44.6848 | 44.9748 | 44.9748 | 45.4548 | 45.4548 | 0.155 | 45.7373
2035-07-01 | 59.0107 |  |  |  |  | 2035-10-01 | 2035-11-01 | 45.4215 | 0.325 | 45.7465 | 45.6115 | 45.7165 | 44.964 | 45.254 | 45.254 | 45.734 | 45.734 | 0.155 | 46.0165
2035-08-01 | 53.6123 |  |  |  |  | 2035-11-01 | 2035-12-01 | 45.2354 | 0.325 | 45.5604 | 45.4254 | 45.5304 | 44.7779 | 45.0679 | 45.0679 | 45.5479 | 45.5479 | 0.155 | 45.8304
2035-09-01 | 45.1423 |  |  |  |  | 2035-12-01 | 2036-01-01 | 46.1661 | 0.325 | 46.4911 | 46.3561 | 46.4611 | 45.7086 | 45.9986 | 45.9986 | 46.4786 | 46.4786 | 0.155 | 46.7611
2035-10-01 | 45.4215 |  |  |  |  | 2036-01-01 | 2036-02-01 | 65.7737 | 0.325 | 66.0987 | 65.9637 | 66.0687 | 65.3162 | 65.6062 | 65.6062 | 66.0862 | 66.0862 | 0.155 | 66.3687
2035-11-01 | 45.2354 |  |  |  |  | 2036-02-01 | 2036-03-01 | 61.2699 | 0.325 | 61.5949 | 61.4599 | 61.5649 | 60.8124 | 61.1024 | 61.1024 | 61.5824 | 61.5824 | 0.155 | 61.8649
2035-12-01 | 46.1661 |  |  |  |  | 2036-03-01 | 2036-04-01 | 50.4797 | 0.325 | 50.8047 | 50.6697 | 50.7747 | 50.0222 | 50.3122 | 50.3122 | 50.7922 | 50.7922 | 0.155 | 51.0747
2036-01-01 | 65.7737 |  |  |  |  | 2036-04-01 | 2036-05-01 | 45.8821 | 0.325 | 46.2071 | 46.0721 | 46.1771 | 45.4246 | 45.7146 | 45.7146 | 46.1946 | 46.1946 | 0.155 | 46.4771
2036-02-01 | 61.2699 |  |  |  |  | 2036-05-01 | 2036-06-01 | 47.4772 | 0.325 | 47.8022 | 47.6672 | 47.7722 | 47.0197 | 47.3097 | 47.3097 | 47.7897 | 47.7897 | 0.155 | 48.0722
2036-03-01 | 50.4797 |  |  |  |  | 2036-06-01 | 2036-07-01 | 47.1018 | 0.325 | 47.4268 | 47.2918 | 47.3968 | 46.6443 | 46.9343 | 46.9343 | 47.4143 | 47.4143 | 0.155 | 47.6968
2036-04-01 | 45.8821 |  |  |  |  | 2036-07-01 | 2036-08-01 | 59.4872 | 0.325 | 59.8122 | 59.6772 | 59.7822 | 59.0297 | 59.3197 | 59.3197 | 59.7997 | 59.7997 | 0.155 | 60.0822
2036-05-01 | 47.4772 |  |  |  |  | 2036-08-01 | 2036-09-01 | 54.0451 | 0.325 | 54.3701 | 54.2351 | 54.3401 | 53.5876 | 53.8776 | 53.8776 | 54.3576 | 54.3576 | 0.155 | 54.6401
2036-06-01 | 47.1018 |  |  |  |  | 2036-09-01 | 2036-10-01 | 45.5068 | 0.325 | 45.8318 | 45.6968 | 45.8018 | 45.0493 | 45.3393 | 45.3393 | 45.8193 | 45.8193 | 0.155 | 46.1018
2036-07-01 | 59.4872 |  |  |  |  | 2036-10-01 | 2036-11-01 | 45.7882 | 0.325 | 46.1132 | 45.9782 | 46.0832 | 45.3307 | 45.6207 | 45.6207 | 46.1007 | 46.1007 | 0.155 | 46.3832
2036-08-01 | 54.0451 |  |  |  |  | 2036-11-01 | 2036-12-01 | 45.6006 | 0.325 | 45.9256 | 45.7906 | 45.8956 | 45.1431 | 45.4331 | 45.4331 | 45.9131 | 45.9131 | 0.155 | 46.1956
2036-09-01 | 45.5068 |  |  |  |  | 2036-12-01 | 2037-01-01 | 46.5389 | 0.325 | 46.8639 | 46.7289 | 46.8339 | 46.0814 | 46.3714 | 46.3714 | 46.8514 | 46.8514 | 0.155 | 47.1339
2036-10-01 | 45.7882 |  |  |  |  | 2037-01-01 | 2037-02-01 | 67.4697 | 0.325 | 67.7947 | 67.6597 | 67.7647 | 67.0122 | 67.3022 | 67.3022 | 67.7822 | 67.7822 | 0.155 | 68.0647
2036-11-01 | 45.6006 |  |  |  |  | 2037-02-01 | 2037-03-01 | 62.8498 | 0.325 | 63.1748 | 63.0398 | 63.1448 | 62.3923 | 62.6823 | 62.6823 | 63.1623 | 63.1623 | 0.155 | 63.4448
2036-12-01 | 46.5389 |  |  |  |  | 2037-03-01 | 2037-04-01 | 51.7813 | 0.325 | 52.1063 | 51.9713 | 52.0763 | 51.3238 | 51.6138 | 51.6138 | 52.0938 | 52.0938 | 0.155 | 52.3763
2037-01-01 | 67.4697 |  |  |  |  | 2037-04-01 | 2037-05-01 | 47.0652 | 0.325 | 47.3902 | 47.2552 | 47.3602 | 46.6077 | 46.8977 | 46.8977 | 47.3777 | 47.3777 | 0.155 | 47.6602
2037-02-01 | 62.8498 |  |  |  |  | 2037-05-01 | 2037-06-01 | 48.7014 | 0.325 | 49.0264 | 48.8914 | 48.9964 | 48.2439 | 48.5339 | 48.5339 | 49.0139 | 49.0139 | 0.155 | 49.2964
2037-03-01 | 51.7813 |  |  |  |  | 2037-06-01 | 2037-07-01 | 48.3164 | 0.325 | 48.6414 | 48.5064 | 48.6114 | 47.8589 | 48.1489 | 48.1489 | 48.6289 | 48.6289 | 0.155 | 48.9114
2037-04-01 | 47.0652 |  |  |  |  | 2037-07-01 | 2037-08-01 | 61.0211 | 0.325 | 61.3461 | 61.2111 | 61.3161 | 60.5636 | 60.8536 | 60.8536 | 61.3336 | 61.3336 | 0.155 | 61.6161
2037-05-01 | 48.7014 |  |  |  |  | 2037-08-01 | 2037-09-01 | 55.4387 | 0.325 | 55.7637 | 55.6287 | 55.7337 | 54.9812 | 55.2712 | 55.2712 | 55.7512 | 55.7512 | 0.155 | 56.0337
2037-06-01 | 48.3164 |  |  |  |  | 2037-09-01 | 2037-10-01 | 46.6802 | 0.325 | 47.0052 | 46.8702 | 46.9752 | 46.2227 | 46.5127 | 46.5127 | 46.9927 | 46.9927 | 0.155 | 47.2752
2037-07-01 | 61.0211 |  |  |  |  | 2037-10-01 | 2037-11-01 | 46.9689 | 0.325 | 47.2939 | 47.1589 | 47.2639 | 46.5114 | 46.8014 | 46.8014 | 47.2814 | 47.2814 | 0.155 | 47.5639
2037-08-01 | 55.4387 |  |  |  |  | 2037-11-01 | 2037-12-01 | 46.7764 | 0.325 | 47.1014 | 46.9664 | 47.0714 | 46.3189 | 46.6089 | 46.6089 | 47.0889 | 47.0889 | 0.155 | 47.3714
2037-09-01 | 46.6802 |  |  |  |  | 2037-12-01 | 2038-01-01 | 47.7389 | 0.325 | 48.0639 | 47.9289 | 48.0339 | 47.2814 | 47.5714 | 47.5714 | 48.0514 | 48.0514 | 0.155 | 48.3339
2037-10-01 | 46.9689 |  |  |  |  | 2038-01-01 | 2038-02-01 | 69.2598 | 0.325 | 69.5848 | 69.4498 | 69.5548 | 68.8023 | 69.0923 | 69.0923 | 69.5723 | 69.5723 | 0.155 | 69.8548
2037-11-01 | 46.7764 |  |  |  |  | 2038-02-01 | 2038-03-01 | 64.5174 | 0.325 | 64.8424 | 64.7074 | 64.8124 | 64.0599 | 64.3499 | 64.3499 | 64.8299 | 64.8299 | 0.155 | 65.1124
2037-12-01 | 47.7389 |  |  |  |  | 2038-03-01 | 2038-04-01 | 53.1552 | 0.325 | 53.4802 | 53.3452 | 53.4502 | 52.6977 | 52.9877 | 52.9877 | 53.4677 | 53.4677 | 0.155 | 53.7502
2038-01-01 | 69.2598 |  |  |  |  | 2038-04-01 | 2038-05-01 | 48.3139 | 0.325 | 48.6389 | 48.5039 | 48.6089 | 47.8564 | 48.1464 | 48.1464 | 48.6264 | 48.6264 | 0.155 | 48.9089
2038-02-01 | 64.5174 |  |  |  |  | 2038-05-01 | 2038-06-01 | 49.9935 | 0.325 | 50.3185 | 50.1835 | 50.2885 | 49.536 | 49.826 | 49.826 | 50.306 | 50.306 | 0.155 | 50.5885
2038-03-01 | 53.1552 |  |  |  |  | 2038-06-01 | 2038-07-01 | 49.5983 | 0.325 | 49.9233 | 49.7883 | 49.8933 | 49.1408 | 49.4308 | 49.4308 | 49.9108 | 49.9108 | 0.155 | 50.1933
2038-04-01 | 48.3139 |  |  |  |  | 2038-07-01 | 2038-08-01 | 62.6401 | 0.325 | 62.9651 | 62.8301 | 62.9351 | 62.1826 | 62.4726 | 62.4726 | 62.9526 | 62.9526 | 0.155 | 63.2351
2038-05-01 | 49.9935 |  |  |  |  | 2038-08-01 | 2038-09-01 | 56.9097 | 0.325 | 57.2347 | 57.0997 | 57.2047 | 56.4522 | 56.7422 | 56.7422 | 57.2222 | 57.2222 | 0.155 | 57.5047
2038-06-01 | 49.5983 |  |  |  |  | 2038-09-01 | 2038-10-01 | 47.9187 | 0.325 | 48.2437 | 48.1087 | 48.2137 | 47.4612 | 47.7512 | 47.7512 | 48.2312 | 48.2312 | 0.155 | 48.5137
2038-07-01 | 62.6401 |  |  |  |  | 2038-10-01 | 2038-11-01 | 48.2151 | 0.325 | 48.5401 | 48.4051 | 48.5101 | 47.7576 | 48.0476 | 48.0476 | 48.5276 | 48.5276 | 0.155 | 48.8101
2038-08-01 | 56.9097 |  |  |  |  | 2038-11-01 | 2038-12-01 | 48.0175 | 0.325 | 48.3425 | 48.2075 | 48.3125 | 47.56 | 47.85 | 47.85 | 48.33 | 48.33 | 0.155 | 48.6125
2038-09-01 | 47.9187 |  |  |  |  | 2038-12-01 | 2039-01-01 | 49.0055 | 0.325 | 49.3305 | 49.1955 | 49.3005 | 48.548 | 48.838 | 48.838 | 49.318 | 49.318 | 0.155 | 49.6005
2038-10-01 | 48.2151 |  |  |  |  | 2039-01-01 | 2039-02-01 | 70.8422 | 0.325 | 71.1672 | 71.0322 | 71.1372 | 70.3847 | 70.6747 | 70.6747 | 71.1547 | 71.1547 | 0.155 | 71.4372
2038-11-01 | 48.0175 |  |  |  |  | 2039-02-01 | 2039-03-01 | 65.9914 | 0.325 | 66.3164 | 66.1814 | 66.2864 | 65.5339 | 65.8239 | 65.8239 | 66.3039 | 66.3039 | 0.155 | 66.5864
2038-12-01 | 49.0055 |  |  |  |  | 2039-03-01 | 2039-04-01 | 54.3696 | 0.325 | 54.6946 | 54.5596 | 54.6646 | 53.9121 | 54.2021 | 54.2021 | 54.6821 | 54.6821 | 0.155 | 54.9646
2039-01-01 | 70.8422 |  |  |  |  | 2039-04-01 | 2039-05-01 | 49.4178 | 0.325 | 49.7428 | 49.6078 | 49.7128 | 48.9603 | 49.2503 | 49.2503 | 49.7303 | 49.7303 | 0.155 | 50.0128
2039-02-01 | 65.9914 |  |  |  |  | 2039-05-01 | 2039-06-01 | 51.1358 | 0.325 | 51.4608 | 51.3258 | 51.4308 | 50.6783 | 50.9683 | 50.9683 | 51.4483 | 51.4483 | 0.155 | 51.7308
2039-03-01 | 54.3696 |  |  |  |  | 2039-06-01 | 2039-07-01 | 50.7315 | 0.325 | 51.0565 | 50.9215 | 51.0265 | 50.274 | 50.564 | 50.564 | 51.044 | 51.044 | 0.155 | 51.3265
2039-04-01 | 49.4178 |  |  |  |  | 2039-07-01 | 2039-08-01 | 64.0713 | 0.325 | 64.3963 | 64.2613 | 64.3663 | 63.6138 | 63.9038 | 63.9038 | 64.3838 | 64.3838 | 0.155 | 64.6663
2039-05-01 | 51.1358 |  |  |  |  | 2039-08-01 | 2039-09-01 | 58.2099 | 0.325 | 58.5349 | 58.3999 | 58.5049 | 57.7524 | 58.0424 | 58.0424 | 58.5224 | 58.5224 | 0.155 | 58.8049
2039-06-01 | 50.7315 |  |  |  |  | 2039-09-01 | 2039-10-01 | 49.0135 | 0.325 | 49.3385 | 49.2035 | 49.3085 | 48.556 | 48.846 | 48.846 | 49.326 | 49.326 | 0.155 | 49.6085
2039-07-01 | 64.0713 |  |  |  |  | 2039-10-01 | 2039-11-01 | 49.3167 | 0.325 | 49.6417 | 49.5067 | 49.6117 | 48.8592 | 49.1492 | 49.1492 | 49.6292 | 49.6292 | 0.155 | 49.9117
2039-08-01 | 58.2099 |  |  |  |  | 2039-11-01 | 2039-12-01 | 49.1146 | 0.325 | 49.4396 | 49.3046 | 49.4096 | 48.6571 | 48.9471 | 48.9471 | 49.4271 | 49.4271 | 0.155 | 49.7096
2039-09-01 | 49.0135 |  |  |  |  | 2039-12-01 | 2040-01-01 | 50.1252 | 0.325 | 50.4502 | 50.3152 | 50.4202 | 49.6677 | 49.9577 | 49.9577 | 50.4377 | 50.4377 | 0.155 | 50.7202
2039-10-01 | 49.3167 |  |  |  |  | 2040-01-01 | 2040-02-01 | 71.4437 | 0.325 | 71.7687 | 71.6337 | 71.7387 | 70.9862 | 71.2762 | 71.2762 | 71.7562 | 71.7562 | 0.155 | 72.0387
2039-11-01 | 49.1146 |  |  |  |  | 2040-02-01 | 2040-03-01 | 66.5517 | 0.325 | 66.8767 | 66.7417 | 66.8467 | 66.0942 | 66.3842 | 66.3842 | 66.8642 | 66.8642 | 0.155 | 67.1467
2039-12-01 | 50.1252 |  |  |  |  | 2040-03-01 | 2040-04-01 | 54.8313 | 0.325 | 55.1563 | 55.0213 | 55.1263 | 54.3738 | 54.6638 | 54.6638 | 55.1438 | 55.1438 | 0.155 | 55.4263
2040-01-01 | 71.4437 |  |  |  |  | 2040-04-01 | 2040-05-01 | 49.8373 | 0.325 | 50.1623 | 50.0273 | 50.1323 | 49.3798 | 49.6698 | 49.6698 | 50.1498 | 50.1498 | 0.155 | 50.4323
2040-02-01 | 66.5517 |  |  |  |  | 2040-05-01 | 2040-06-01 | 51.5699 | 0.325 | 51.8949 | 51.7599 | 51.8649 | 51.1124 | 51.4024 | 51.4024 | 51.8824 | 51.8824 | 0.155 | 52.1649
2040-03-01 | 54.8313 |  |  |  |  | 2040-06-01 | 2040-07-01 | 51.1623 | 0.325 | 51.4873 | 51.3523 | 51.4573 | 50.7048 | 50.9948 | 50.9948 | 51.4748 | 51.4748 | 0.155 | 51.7573
2040-04-01 | 49.8373 |  |  |  |  | 2040-07-01 | 2040-08-01 | 64.6153 | 0.325 | 64.9403 | 64.8053 | 64.9103 | 64.1578 | 64.4478 | 64.4478 | 64.9278 | 64.9278 | 0.155 | 65.2103
2040-05-01 | 51.5699 |  |  |  |  | 2040-08-01 | 2040-09-01 | 58.7041 | 0.325 | 59.0291 | 58.8941 | 58.9991 | 58.2466 | 58.5366 | 58.5366 | 59.0166 | 59.0166 | 0.155 | 59.2991
2040-06-01 | 51.1623 |  |  |  |  | 2040-09-01 | 2040-10-01 | 49.4297 | 0.325 | 49.7547 | 49.6197 | 49.7247 | 48.9722 | 49.2622 | 49.2622 | 49.7422 | 49.7422 | 0.155 | 50.0247
2040-07-01 | 64.6153 |  |  |  |  | 2040-10-01 | 2040-11-01 | 49.7354 | 0.325 | 50.0604 | 49.9254 | 50.0304 | 49.2779 | 49.5679 | 49.5679 | 50.0479 | 50.0479 | 0.155 | 50.3304
2040-08-01 | 58.7041 |  |  |  |  | 2040-11-01 | 2040-12-01 | 49.5316 | 0.325 | 49.8566 | 49.7216 | 49.8266 | 49.0741 | 49.3641 | 49.3641 | 49.8441 | 49.8441 | 0.155 | 50.1266
2040-09-01 | 49.4297 |  |  |  |  | 2040-12-01 | 2041-01-01 | 50.5508 | 0.325 | 50.8758 | 50.7408 | 50.8458 | 50.0933 | 50.3833 | 50.3833 | 50.8633 | 50.8633 | 0.155 | 51.1458
2040-10-01 | 49.7354
2040-11-01 | 49.5316
2040-12-01 | 50.5508

## Off Peak
| off peak | EIA Escalation
2016-09-01 | 14.11 | 2019 | 9.36% |  |  | STARTDATE | ENDDATE | SPP off pk | Aberdeen 1 | Aberdeen 2 | Beethoven | Big Stone | Coyote | Huron 1 | Huron 2 | Neal 4 | Oak Tree | Titan | Load
2016-10-01 | 16.77 | 2020 | 8.982% | Location | DA Basis vs. North Hub 10-5-2016 | 2017-01-01 | 2017-02-01 | 25.25 | 25.575 | 25.575 | 25.44 | 25.545 | 24.7925 | 25.0825 | 25.0825 | 25.5625 | 25.5625 | 25.405 | 25.845
2016-11-01 | 16.05 | 2021 | 4.945% | SPP North Hub |  | 2017-02-01 | 2017-03-01 | 22 | 22.325 | 22.325 | 22.19 | 22.295 | 21.5425 | 21.8325 | 21.8325 | 22.3125 | 22.3125 | 22.155 | 22.595
2016-12-01 | 16.85 | 2022 | 3.552% |  |  | 2017-03-01 | 2017-04-01 | 17.9 | 18.225 | 18.225 | 18.09 | 18.195 | 17.4425 | 17.7325 | 17.7325 | 18.2125 | 18.2125 | 18.055 | 18.495
2017-01-01 | 25.25 | 2023 | 6.201% | Aberdeen 1 | 0.325 | 2017-04-01 | 2017-05-01 | 14 | 14.325 | 14.325 | 14.19 | 14.295 | 13.5425 | 13.8325 | 13.8325 | 14.3125 | 14.3125 | 14.155 | 14.595
2017-02-01 | 22 | 2024 | 4.598% | Aberdeen 2 | 0.325 | 2017-05-01 | 2017-06-01 | 15.95 | 16.275 | 16.275 | 16.14 | 16.245 | 15.4925 | 15.7825 | 15.7825 | 16.2625 | 16.2625 | 16.105 | 16.545
2017-03-01 | 17.9 | 2025 | 4.797% | Beethoven | 0.19 | 2017-06-01 | 2017-07-01 | 15.55 | 15.875 | 15.875 | 15.74 | 15.845 | 15.0925 | 15.3825 | 15.3825 | 15.8625 | 15.8625 | 15.705 | 16.145
2017-04-01 | 14 | 2026 | 1.908% | Big Stone | 0.295 | 2017-07-01 | 2017-08-01 | 17.85 | 18.175 | 18.175 | 18.04 | 18.145 | 17.3925 | 17.6825 | 17.6825 | 18.1625 | 18.1625 | 18.005 | 18.445
2017-05-01 | 15.95 | 2027 | 0.00289% | Coyote | -0.4575 | 2017-08-01 | 2017-09-01 | 15.55 | 15.875 | 15.875 | 15.74 | 15.845 | 15.0925 | 15.3825 | 15.3825 | 15.8625 | 15.8625 | 15.705 | 16.145
2017-06-01 | 15.55 | 2028 | 1.056% | Huron 1 | -0.1675 | 2017-09-01 | 2017-10-01 | 16.1 | 16.425 | 16.425 | 16.29 | 16.395 | 15.6425 | 15.9325 | 15.9325 | 16.4125 | 16.4125 | 16.255 | 16.695
2017-07-01 | 17.85 | 2029 | 1.094% | Huron 2 | -0.1675 | 2017-10-01 | 2017-11-01 | 17.05 | 17.375 | 17.375 | 17.24 | 17.345 | 16.5925 | 16.8825 | 16.8825 | 17.3625 | 17.3625 | 17.205 | 17.645
2017-08-01 | 15.55 | 2030 | 1.694% | Neal 4 | 0.3125 | 2017-11-01 | 2017-12-01 | 16.3 | 16.625 | 16.625 | 16.49 | 16.595 | 15.8425 | 16.1325 | 16.1325 | 16.6125 | 16.6125 | 16.455 | 16.895
2017-09-01 | 16.1 | 2031 | 2.586% | Oak Tree | 0.3125 | 2017-12-01 | 2018-01-01 | 19.95 | 20.275 | 20.275 | 20.14 | 20.245 | 19.4925 | 19.7825 | 19.7825 | 20.2625 | 20.2625 | 20.105 | 20.545
2017-10-01 | 17.05 | 2032 | 4.517% | Titan | -0.17 | 2018-01-01 | 2018-02-01 | 26.45 | 26.775 | 26.775 | 26.64 | 26.745 | 25.9925 | 26.2825 | 26.2825 | 26.7625 | 26.7625 | 26.605 | 27.045
2017-11-01 | 16.3 | 2033 | 3.184% | Load | 0.27 | 2018-02-01 | 2018-03-01 | 24.1 | 24.425 | 24.425 | 24.29 | 24.395 | 23.6425 | 23.9325 | 23.9325 | 24.4125 | 24.4125 | 24.255 | 24.695
2017-12-01 | 19.95 | 2034 | 3.126% |  |  | 2018-03-01 | 2018-04-01 | 19.55 | 19.875 | 19.875 | 19.74 | 19.845 | 19.0925 | 19.3825 | 19.3825 | 19.8625 | 19.8625 | 19.705 | 20.145
2018-01-01 | 26.45 | 2035 | 2.206% |  |  | 2018-04-01 | 2018-05-01 | 18.45 | 18.775 | 18.775 | 18.64 | 18.745 | 17.9925 | 18.2825 | 18.2825 | 18.7625 | 18.7625 | 18.605 | 19.045
2018-02-01 | 24.1 | 2036 | 0.8074% |  |  | 2018-05-01 | 2018-06-01 | 14.55 | 14.875 | 14.875 | 14.74 | 14.845 | 14.0925 | 14.3825 | 14.3825 | 14.8625 | 14.8625 | 14.705 | 15.145
2018-03-01 | 19.55 | 2037 | 2.579% |  |  | 2018-06-01 | 2018-07-01 | 15.2 | 15.525 | 15.525 | 15.39 | 15.495 | 14.7425 | 15.0325 | 15.0325 | 15.5125 | 15.5125 | 15.355 | 15.795
2018-04-01 | 18.45 | 2038 | 2.653% |  |  | 2018-07-01 | 2018-08-01 | 16.85 | 17.175 | 17.175 | 17.04 | 17.145 | 16.3925 | 16.6825 | 16.6825 | 17.1625 | 17.1625 | 17.005 | 17.445
2018-05-01 | 14.55 | 2039 | 2.285% |  |  | 2018-08-01 | 2018-09-01 | 16.5 | 16.825 | 16.825 | 16.69 | 16.795 | 16.0425 | 16.3325 | 16.3325 | 16.8125 | 16.8125 | 16.655 | 17.095
2018-06-01 | 15.2 | 2040 | 0.849% |  |  | 2018-09-01 | 2018-10-01 | 14.5 | 14.825 | 14.825 | 14.69 | 14.795 | 14.0425 | 14.3325 | 14.3325 | 14.8125 | 14.8125 | 14.655 | 15.095
2018-07-01 | 16.85 |  |  |  |  | 2018-10-01 | 2018-11-01 | 16.1 | 16.425 | 16.425 | 16.29 | 16.395 | 15.6425 | 15.9325 | 15.9325 | 16.4125 | 16.4125 | 16.255 | 16.695
2018-08-01 | 16.5 |  |  |  |  | 2018-11-01 | 2018-12-01 | 16.95 | 17.275 | 17.275 | 17.14 | 17.245 | 16.4925 | 16.7825 | 16.7825 | 17.2625 | 17.2625 | 17.105 | 17.545
2018-09-01 | 14.5 |  |  |  |  | 2018-12-01 | 2019-01-01 | 17.7 | 18.025 | 18.025 | 17.89 | 17.995 | 17.2425 | 17.5325 | 17.5325 | 18.0125 | 18.0125 | 17.855 | 18.295
2018-10-01 | 16.1 |  |  |  |  | 2019-01-01 | 2019-02-01 | 28.9257 | 29.2507 | 29.2507 | 29.1157 | 29.2207 | 28.4682 | 28.7582 | 28.7582 | 29.2382 | 29.2382 | 29.0807 | 29.5207
2018-11-01 | 16.95 |  |  |  |  | 2019-02-01 | 2019-03-01 | 26.3557 | 26.6807 | 26.6807 | 26.5457 | 26.6507 | 25.8982 | 26.1882 | 26.1882 | 26.6682 | 26.6682 | 26.5107 | 26.9507
2018-12-01 | 17.7 |  |  |  |  | 2019-03-01 | 2019-04-01 | 21.3798 | 21.7048 | 21.7048 | 21.5698 | 21.6748 | 20.9223 | 21.2123 | 21.2123 | 21.6923 | 21.6923 | 21.5348 | 21.9748
2019-01-01 | 28.9257 |  |  |  |  | 2019-04-01 | 2019-05-01 | 20.1769 | 20.5019 | 20.5019 | 20.3669 | 20.4719 | 19.7194 | 20.0094 | 20.0094 | 20.4894 | 20.4894 | 20.3319 | 20.7719
2019-02-01 | 26.3557 |  |  |  |  | 2019-05-01 | 2019-06-01 | 15.9119 | 16.2369 | 16.2369 | 16.1019 | 16.2069 | 15.4544 | 15.7444 | 15.7444 | 16.2244 | 16.2244 | 16.0669 | 16.5069
2019-03-01 | 21.3798 |  |  |  |  | 2019-06-01 | 2019-07-01 | 16.6227 | 16.9477 | 16.9477 | 16.8127 | 16.9177 | 16.1652 | 16.4552 | 16.4552 | 16.9352 | 16.9352 | 16.7777 | 17.2177
2019-04-01 | 20.1769 |  |  |  |  | 2019-07-01 | 2019-08-01 | 18.4271 | 18.7521 | 18.7521 | 18.6171 | 18.7221 | 17.9696 | 18.2596 | 18.2596 | 18.7396 | 18.7396 | 18.5821 | 19.0221
2019-05-01 | 15.9119 |  |  |  |  | 2019-08-01 | 2019-09-01 | 18.0444 | 18.3694 | 18.3694 | 18.2344 | 18.3394 | 17.5869 | 17.8769 | 17.8769 | 18.3569 | 18.3569 | 18.1994 | 18.6394
2019-06-01 | 16.6227 |  |  |  |  | 2019-09-01 | 2019-10-01 | 15.8572 | 16.1822 | 16.1822 | 16.0472 | 16.1522 | 15.3997 | 15.6897 | 15.6897 | 16.1697 | 16.1697 | 16.0122 | 16.4522
2019-07-01 | 18.4271 |  |  |  |  | 2019-10-01 | 2019-11-01 | 17.6069 | 17.9319 | 17.9319 | 17.7969 | 17.9019 | 17.1494 | 17.4394 | 17.4394 | 17.9194 | 17.9194 | 17.7619 | 18.2019
2019-08-01 | 18.0444 |  |  |  |  | 2019-11-01 | 2019-12-01 | 18.5365 | 18.8615 | 18.8615 | 18.7265 | 18.8315 | 18.079 | 18.369 | 18.369 | 18.849 | 18.849 | 18.6915 | 19.1315
2019-09-01 | 15.8572 |  |  |  |  | 2019-12-01 | 2020-01-01 | 19.3567 | 19.6817 | 19.6817 | 19.5467 | 19.6517 | 18.8992 | 19.1892 | 19.1892 | 19.6692 | 19.6692 | 19.5117 | 19.9517
2019-10-01 | 17.6069 |  |  |  |  | 2020-01-01 | 2020-02-01 | 31.5237 | 31.8487 | 31.8487 | 31.7137 | 31.8187 | 31.0662 | 31.3562 | 31.3562 | 31.8362 | 31.8362 | 31.6787 | 32.1187
2019-11-01 | 18.5365 |  |  |  |  | 2020-02-01 | 2020-03-01 | 28.7229 | 29.0479 | 29.0479 | 28.9129 | 29.0179 | 28.2654 | 28.5554 | 28.5554 | 29.0354 | 29.0354 | 28.8779 | 29.3179
2019-12-01 | 19.3567 |  |  |  |  | 2020-03-01 | 2020-04-01 | 23.3001 | 23.6251 | 23.6251 | 23.4901 | 23.5951 | 22.8426 | 23.1326 | 23.1326 | 23.6126 | 23.6126 | 23.4551 | 23.8951
2020-01-01 | 31.5237 |  |  |  |  | 2020-04-01 | 2020-05-01 | 21.9891 | 22.3141 | 22.3141 | 22.1791 | 22.2841 | 21.5316 | 21.8216 | 21.8216 | 22.3016 | 22.3016 | 22.1441 | 22.5841
2020-02-01 | 28.7229 |  |  |  |  | 2020-05-01 | 2020-06-01 | 17.341 | 17.666 | 17.666 | 17.531 | 17.636 | 16.8835 | 17.1735 | 17.1735 | 17.6535 | 17.6535 | 17.496 | 17.936
2020-03-01 | 23.3001 |  |  |  |  | 2020-06-01 | 2020-07-01 | 18.1157 | 18.4407 | 18.4407 | 18.3057 | 18.4107 | 17.6582 | 17.9482 | 17.9482 | 18.4282 | 18.4282 | 18.2707 | 18.7107
2020-04-01 | 21.9891 |  |  |  |  | 2020-07-01 | 2020-08-01 | 20.0822 | 20.4072 | 20.4072 | 20.2722 | 20.3772 | 19.6247 | 19.9147 | 19.9147 | 20.3947 | 20.3947 | 20.2372 | 20.6772
2020-05-01 | 17.341 |  |  |  |  | 2020-08-01 | 2020-09-01 | 19.6651 | 19.9901 | 19.9901 | 19.8551 | 19.9601 | 19.2076 | 19.4976 | 19.4976 | 19.9776 | 19.9776 | 19.8201 | 20.2601
2020-06-01 | 18.1157 |  |  |  |  | 2020-09-01 | 2020-10-01 | 17.2814 | 17.6064 | 17.6064 | 17.4714 | 17.5764 | 16.8239 | 17.1139 | 17.1139 | 17.5939 | 17.5939 | 17.4364 | 17.8764
2020-07-01 | 20.0822 |  |  |  |  | 2020-10-01 | 2020-11-01 | 19.1883 | 19.5133 | 19.5133 | 19.3783 | 19.4833 | 18.7308 | 19.0208 | 19.0208 | 19.5008 | 19.5008 | 19.3433 | 19.7833
2020-08-01 | 19.6651 |  |  |  |  | 2020-11-01 | 2020-12-01 | 20.2014 | 20.5264 | 20.5264 | 20.3914 | 20.4964 | 19.7439 | 20.0339 | 20.0339 | 20.5139 | 20.5139 | 20.3564 | 20.7964
2020-09-01 | 17.2814 |  |  |  |  | 2020-12-01 | 2021-01-01 | 21.0952 | 21.4202 | 21.4202 | 21.2852 | 21.3902 | 20.6377 | 20.9277 | 20.9277 | 21.4077 | 21.4077 | 21.2502 | 21.6902
2020-10-01 | 19.1883 |  |  |  |  | 2021-01-01 | 2021-02-01 | 33.0825 | 33.4075 | 33.4075 | 33.2725 | 33.3775 | 32.625 | 32.915 | 32.915 | 33.395 | 33.395 | 33.2375 | 33.6775
2020-11-01 | 20.2014 |  |  |  |  | 2021-02-01 | 2021-03-01 | 30.1432 | 30.4682 | 30.4682 | 30.3332 | 30.4382 | 29.6857 | 29.9757 | 29.9757 | 30.4557 | 30.4557 | 30.2982 | 30.7382
2020-12-01 | 21.0952 |  |  |  |  | 2021-03-01 | 2021-04-01 | 24.4523 | 24.7773 | 24.7773 | 24.6423 | 24.7473 | 23.9948 | 24.2848 | 24.2848 | 24.7648 | 24.7648 | 24.6073 | 25.0473
2021-01-01 | 33.0825 |  |  |  |  | 2021-04-01 | 2021-05-01 | 23.0765 | 23.4015 | 23.4015 | 23.2665 | 23.3715 | 22.619 | 22.909 | 22.909 | 23.389 | 23.389 | 23.2315 | 23.6715
2021-02-01 | 30.1432 |  |  |  |  | 2021-05-01 | 2021-06-01 | 18.1985 | 18.5235 | 18.5235 | 18.3885 | 18.4935 | 17.741 | 18.031 | 18.031 | 18.511 | 18.511 | 18.3535 | 18.7935
2021-03-01 | 24.4523 |  |  |  |  | 2021-06-01 | 2021-07-01 | 19.0115 | 19.3365 | 19.3365 | 19.2015 | 19.3065 | 18.554 | 18.844 | 18.844 | 19.324 | 19.324 | 19.1665 | 19.6065
2021-04-01 | 23.0765 |  |  |  |  | 2021-07-01 | 2021-08-01 | 21.0753 | 21.4003 | 21.4003 | 21.2653 | 21.3703 | 20.6178 | 20.9078 | 20.9078 | 21.3878 | 21.3878 | 21.2303 | 21.6703
2021-05-01 | 18.1985 |  |  |  |  | 2021-08-01 | 2021-09-01 | 20.6375 | 20.9625 | 20.9625 | 20.8275 | 20.9325 | 20.18 | 20.47 | 20.47 | 20.95 | 20.95 | 20.7925 | 21.2325
2021-06-01 | 19.0115 |  |  |  |  | 2021-09-01 | 2021-10-01 | 18.136 | 18.461 | 18.461 | 18.326 | 18.431 | 17.6785 | 17.9685 | 17.9685 | 18.4485 | 18.4485 | 18.291 | 18.731
2021-07-01 | 21.0753 |  |  |  |  | 2021-10-01 | 2021-11-01 | 20.1372 | 20.4622 | 20.4622 | 20.3272 | 20.4322 | 19.6797 | 19.9697 | 19.9697 | 20.4497 | 20.4497 | 20.2922 | 20.7322
2021-08-01 | 20.6375 |  |  |  |  | 2021-11-01 | 2021-12-01 | 21.2003 | 21.5253 | 21.5253 | 21.3903 | 21.4953 | 20.7428 | 21.0328 | 21.0328 | 21.5128 | 21.5128 | 21.3553 | 21.7953
2021-09-01 | 18.136 |  |  |  |  | 2021-12-01 | 2022-01-01 | 22.1384 | 22.4634 | 22.4634 | 22.3284 | 22.4334 | 21.6809 | 21.9709 | 21.9709 | 22.4509 | 22.4509 | 22.2934 | 22.7334
2021-10-01 | 20.1372 |  |  |  |  | 2022-01-01 | 2022-02-01 | 34.2578 | 34.5828 | 34.5828 | 34.4478 | 34.5528 | 33.8003 | 34.0903 | 34.0903 | 34.5703 | 34.5703 | 34.4128 | 34.8528
2021-11-01 | 21.2003 |  |  |  |  | 2022-02-01 | 2022-03-01 | 31.2141 | 31.5391 | 31.5391 | 31.4041 | 31.5091 | 30.7566 | 31.0466 | 31.0466 | 31.5266 | 31.5266 | 31.3691 | 31.8091
2021-12-01 | 22.1384 |  |  |  |  | 2022-03-01 | 2022-04-01 | 25.321 | 25.646 | 25.646 | 25.511 | 25.616 | 24.8635 | 25.1535 | 25.1535 | 25.6335 | 25.6335 | 25.476 | 25.916
2022-01-01 | 34.2578 |  |  |  |  | 2022-04-01 | 2022-05-01 | 23.8963 | 24.2213 | 24.2213 | 24.0863 | 24.1913 | 23.4388 | 23.7288 | 23.7288 | 24.2088 | 24.2088 | 24.0513 | 24.4913
2022-02-01 | 31.2141 |  |  |  |  | 2022-05-01 | 2022-06-01 | 18.845 | 19.17 | 19.17 | 19.035 | 19.14 | 18.3875 | 18.6775 | 18.6775 | 19.1575 | 19.1575 | 19 | 19.44
2022-03-01 | 25.321 |  |  |  |  | 2022-06-01 | 2022-07-01 | 19.6869 | 20.0119 | 20.0119 | 19.8769 | 19.9819 | 19.2294 | 19.5194 | 19.5194 | 19.9994 | 19.9994 | 19.8419 | 20.2819
2022-04-01 | 23.8963 |  |  |  |  | 2022-07-01 | 2022-08-01 | 21.8239 | 22.1489 | 22.1489 | 22.0139 | 22.1189 | 21.3664 | 21.6564 | 21.6564 | 22.1364 | 22.1364 | 21.9789 | 22.4189
2022-05-01 | 18.845 |  |  |  |  | 2022-08-01 | 2022-09-01 | 21.3706 | 21.6956 | 21.6956 | 21.5606 | 21.6656 | 20.9131 | 21.2031 | 21.2031 | 21.6831 | 21.6831 | 21.5256 | 21.9656
2022-06-01 | 19.6869 |  |  |  |  | 2022-09-01 | 2022-10-01 | 18.7803 | 19.1053 | 19.1053 | 18.9703 | 19.0753 | 18.3228 | 18.6128 | 18.6128 | 19.0928 | 19.0928 | 18.9353 | 19.3753
2022-07-01 | 21.8239 |  |  |  |  | 2022-10-01 | 2022-11-01 | 20.8526 | 21.1776 | 21.1776 | 21.0426 | 21.1476 | 20.3951 | 20.6851 | 20.6851 | 21.1651 | 21.1651 | 21.0076 | 21.4476
2022-08-01 | 21.3706 |  |  |  |  | 2022-11-01 | 2022-12-01 | 21.9535 | 22.2785 | 22.2785 | 22.1435 | 22.2485 | 21.496 | 21.786 | 21.786 | 22.266 | 22.266 | 22.1085 | 22.5485
2022-09-01 | 18.7803 |  |  |  |  | 2022-12-01 | 2023-01-01 | 22.9249 | 23.2499 | 23.2499 | 23.1149 | 23.2199 | 22.4674 | 22.7574 | 22.7574 | 23.2374 | 23.2374 | 23.0799 | 23.5199
2022-10-01 | 20.8526 |  |  |  |  | 2023-01-01 | 2023-02-01 | 36.382 | 36.707 | 36.707 | 36.572 | 36.677 | 35.9245 | 36.2145 | 36.2145 | 36.6945 | 36.6945 | 36.537 | 36.977
2022-11-01 | 21.9535 |  |  |  |  | 2023-02-01 | 2023-03-01 | 33.1496 | 33.4746 | 33.4746 | 33.3396 | 33.4446 | 32.6921 | 32.9821 | 32.9821 | 33.4621 | 33.4621 | 33.3046 | 33.7446
2022-12-01 | 22.9249 |  |  |  |  | 2023-03-01 | 2023-04-01 | 26.891 | 27.216 | 27.216 | 27.081 | 27.186 | 26.4335 | 26.7235 | 26.7235 | 27.2035 | 27.2035 | 27.046 | 27.486
2023-01-01 | 36.382 |  |  |  |  | 2023-04-01 | 2023-05-01 | 25.378 | 25.703 | 25.703 | 25.568 | 25.673 | 24.9205 | 25.2105 | 25.2105 | 25.6905 | 25.6905 | 25.533 | 25.973
2023-02-01 | 33.1496 |  |  |  |  | 2023-05-01 | 2023-06-01 | 20.0135 | 20.3385 | 20.3385 | 20.2035 | 20.3085 | 19.556 | 19.846 | 19.846 | 20.326 | 20.326 | 20.1685 | 20.6085
2023-03-01 | 26.891 |  |  |  |  | 2023-06-01 | 2023-07-01 | 20.9076 | 21.2326 | 21.2326 | 21.0976 | 21.2026 | 20.4501 | 20.7401 | 20.7401 | 21.2201 | 21.2201 | 21.0626 | 21.5026
2023-04-01 | 25.378 |  |  |  |  | 2023-07-01 | 2023-08-01 | 23.1772 | 23.5022 | 23.5022 | 23.3672 | 23.4722 | 22.7197 | 23.0097 | 23.0097 | 23.4897 | 23.4897 | 23.3322 | 23.7722
2023-05-01 | 20.0135 |  |  |  |  | 2023-08-01 | 2023-09-01 | 22.6958 | 23.0208 | 23.0208 | 22.8858 | 22.9908 | 22.2383 | 22.5283 | 22.5283 | 23.0083 | 23.0083 | 22.8508 | 23.2908
2023-06-01 | 20.9076 |  |  |  |  | 2023-09-01 | 2023-10-01 | 19.9448 | 20.2698 | 20.2698 | 20.1348 | 20.2398 | 19.4873 | 19.7773 | 19.7773 | 20.2573 | 20.2573 | 20.0998 | 20.5398
2023-07-01 | 23.1772 |  |  |  |  | 2023-10-01 | 2023-11-01 | 22.1456 | 22.4706 | 22.4706 | 22.3356 | 22.4406 | 21.6881 | 21.9781 | 21.9781 | 22.4581 | 22.4581 | 22.3006 | 22.7406
2023-08-01 | 22.6958 |  |  |  |  | 2023-11-01 | 2023-12-01 | 23.3147 | 23.6397 | 23.6397 | 23.5047 | 23.6097 | 22.8572 | 23.1472 | 23.1472 | 23.6272 | 23.6272 | 23.4697 | 23.9097
2023-09-01 | 19.9448 |  |  |  |  | 2023-12-01 | 2024-01-01 | 24.3464 | 24.6714 | 24.6714 | 24.5364 | 24.6414 | 23.8889 | 24.1789 | 24.1789 | 24.6589 | 24.6589 | 24.5014 | 24.9414
2023-10-01 | 22.1456 |  |  |  |  | 2024-01-01 | 2024-02-01 | 38.0549 | 38.3799 | 38.3799 | 38.2449 | 38.3499 | 37.5974 | 37.8874 | 37.8874 | 38.3674 | 38.3674 | 38.2099 | 38.6499
2023-11-01 | 23.3147 |  |  |  |  | 2024-02-01 | 2024-03-01 | 34.6739 | 34.9989 | 34.9989 | 34.8639 | 34.9689 | 34.2164 | 34.5064 | 34.5064 | 34.9864 | 34.9864 | 34.8289 | 35.2689
2023-12-01 | 24.3464 |  |  |  |  | 2024-03-01 | 2024-04-01 | 28.1276 | 28.4526 | 28.4526 | 28.3176 | 28.4226 | 27.6701 | 27.9601 | 27.9601 | 28.4401 | 28.4401 | 28.2826 | 28.7226
2024-01-01 | 38.0549 |  |  |  |  | 2024-04-01 | 2024-05-01 | 26.5449 | 26.8699 | 26.8699 | 26.7349 | 26.8399 | 26.0874 | 26.3774 | 26.3774 | 26.8574 | 26.8574 | 26.6999 | 27.1399
2024-02-01 | 34.6739 |  |  |  |  | 2024-05-01 | 2024-06-01 | 20.9338 | 21.2588 | 21.2588 | 21.1238 | 21.2288 | 20.4763 | 20.7663 | 20.7663 | 21.2463 | 21.2463 | 21.0888 | 21.5288
2024-03-01 | 28.1276 |  |  |  |  | 2024-06-01 | 2024-07-01 | 21.869 | 22.194 | 22.194 | 22.059 | 22.164 | 21.4115 | 21.7015 | 21.7015 | 22.1815 | 22.1815 | 22.024 | 22.464
2024-04-01 | 26.5449 |  |  |  |  | 2024-07-01 | 2024-08-01 | 24.2429 | 24.5679 | 24.5679 | 24.4329 | 24.5379 | 23.7854 | 24.0754 | 24.0754 | 24.5554 | 24.5554 | 24.3979 | 24.8379
2024-05-01 | 20.9338 |  |  |  |  | 2024-08-01 | 2024-09-01 | 23.7394 | 24.0644 | 24.0644 | 23.9294 | 24.0344 | 23.2819 | 23.5719 | 23.5719 | 24.0519 | 24.0519 | 23.8944 | 24.3344
2024-06-01 | 21.869 |  |  |  |  | 2024-09-01 | 2024-10-01 | 20.8619 | 21.1869 | 21.1869 | 21.0519 | 21.1569 | 20.4044 | 20.6944 | 20.6944 | 21.1744 | 21.1744 | 21.0169 | 21.4569
2024-07-01 | 24.2429 |  |  |  |  | 2024-10-01 | 2024-11-01 | 23.1639 | 23.4889 | 23.4889 | 23.3539 | 23.4589 | 22.7064 | 22.9964 | 22.9964 | 23.4764 | 23.4764 | 23.3189 | 23.7589
2024-08-01 | 23.7394 |  |  |  |  | 2024-11-01 | 2024-12-01 | 24.3868 | 24.7118 | 24.7118 | 24.5768 | 24.6818 | 23.9293 | 24.2193 | 24.2193 | 24.6993 | 24.6993 | 24.5418 | 24.9818
2024-09-01 | 20.8619 |  |  |  |  | 2024-12-01 | 2025-01-01 | 25.4659 | 25.7909 | 25.7909 | 25.6559 | 25.7609 | 25.0084 | 25.2984 | 25.2984 | 25.7784 | 25.7784 | 25.6209 | 26.0609
2024-10-01 | 23.1639 |  |  |  |  | 2025-01-01 | 2025-02-01 | 39.8805 | 40.2055 | 40.2055 | 40.0705 | 40.1755 | 39.423 | 39.713 | 39.713 | 40.193 | 40.193 | 40.0355 | 40.4755
2024-11-01 | 24.3868 |  |  |  |  | 2025-02-01 | 2025-03-01 | 36.3372 | 36.6622 | 36.6622 | 36.5272 | 36.6322 | 35.8797 | 36.1697 | 36.1697 | 36.6497 | 36.6497 | 36.4922 | 36.9322
2024-12-01 | 25.4659 |  |  |  |  | 2025-03-01 | 2025-04-01 | 29.4769 | 29.8019 | 29.8019 | 29.6669 | 29.7719 | 29.0194 | 29.3094 | 29.3094 | 29.7894 | 29.7894 | 29.6319 | 30.0719
2025-01-01 | 39.8805 |  |  |  |  | 2025-04-01 | 2025-05-01 | 27.8183 | 28.1433 | 28.1433 | 28.0083 | 28.1133 | 27.3608 | 27.6508 | 27.6508 | 28.1308 | 28.1308 | 27.9733 | 28.4133
2025-02-01 | 36.3372 |  |  |  |  | 2025-05-01 | 2025-06-01 | 21.938 | 22.263 | 22.263 | 22.128 | 22.233 | 21.4805 | 21.7705 | 21.7705 | 22.2505 | 22.2505 | 22.093 | 22.533
2025-03-01 | 29.4769 |  |  |  |  | 2025-06-01 | 2025-07-01 | 22.9181 | 23.2431 | 23.2431 | 23.1081 | 23.2131 | 22.4606 | 22.7506 | 22.7506 | 23.2306 | 23.2306 | 23.0731 | 23.5131
2025-04-01 | 27.8183 |  |  |  |  | 2025-07-01 | 2025-08-01 | 25.4059 | 25.7309 | 25.7309 | 25.5959 | 25.7009 | 24.9484 | 25.2384 | 25.2384 | 25.7184 | 25.7184 | 25.5609 | 26.0009
2025-05-01 | 21.938 |  |  |  |  | 2025-08-01 | 2025-09-01 | 24.8782 | 25.2032 | 25.2032 | 25.0682 | 25.1732 | 24.4207 | 24.7107 | 24.7107 | 25.1907 | 25.1907 | 25.0332 | 25.4732
2025-06-01 | 22.9181 |  |  |  |  | 2025-09-01 | 2025-10-01 | 21.8626 | 22.1876 | 22.1876 | 22.0526 | 22.1576 | 21.4051 | 21.6951 | 21.6951 | 22.1751 | 22.1751 | 22.0176 | 22.4576
2025-07-01 | 25.4059 |  |  |  |  | 2025-10-01 | 2025-11-01 | 24.2751 | 24.6001 | 24.6001 | 24.4651 | 24.5701 | 23.8176 | 24.1076 | 24.1076 | 24.5876 | 24.5876 | 24.4301 | 24.8701
2025-08-01 | 24.8782 |  |  |  |  | 2025-11-01 | 2025-12-01 | 25.5567 | 25.8817 | 25.8817 | 25.7467 | 25.8517 | 25.0992 | 25.3892 | 25.3892 | 25.8692 | 25.8692 | 25.7117 | 26.1517
2025-09-01 | 21.8626 |  |  |  |  | 2025-12-01 | 2026-01-01 | 26.6875 | 27.0125 | 27.0125 | 26.8775 | 26.9825 | 26.23 | 26.52 | 26.52 | 27 | 27 | 26.8425 | 27.2825
2025-10-01 | 24.2751 |  |  |  |  | 2026-01-01 | 2026-02-01 | 40.6416 | 40.9666 | 40.9666 | 40.8316 | 40.9366 | 40.1841 | 40.4741 | 40.4741 | 40.9541 | 40.9541 | 40.7966 | 41.2366
2025-11-01 | 25.5567 |  |  |  |  | 2026-02-01 | 2026-03-01 | 37.0307 | 37.3557 | 37.3557 | 37.2207 | 37.3257 | 36.5732 | 36.8632 | 36.8632 | 37.3432 | 37.3432 | 37.1857 | 37.6257
2025-12-01 | 26.6875 |  |  |  |  | 2026-03-01 | 2026-04-01 | 30.0394 | 30.3644 | 30.3644 | 30.2294 | 30.3344 | 29.5819 | 29.8719 | 29.8719 | 30.3519 | 30.3519 | 30.1944 | 30.6344
2026-01-01 | 40.6416 |  |  |  |  | 2026-04-01 | 2026-05-01 | 28.3492 | 28.6742 | 28.6742 | 28.5392 | 28.6442 | 27.8917 | 28.1817 | 28.1817 | 28.6617 | 28.6617 | 28.5042 | 28.9442
2026-02-01 | 37.0307 |  |  |  |  | 2026-05-01 | 2026-06-01 | 22.3567 | 22.6817 | 22.6817 | 22.5467 | 22.6517 | 21.8992 | 22.1892 | 22.1892 | 22.6692 | 22.6692 | 22.5117 | 22.9517
2026-03-01 | 30.0394 |  |  |  |  | 2026-06-01 | 2026-07-01 | 23.3554 | 23.6804 | 23.6804 | 23.5454 | 23.6504 | 22.8979 | 23.1879 | 23.1879 | 23.6679 | 23.6679 | 23.5104 | 23.9504
2026-04-01 | 28.3492 |  |  |  |  | 2026-07-01 | 2026-08-01 | 25.8907 | 26.2157 | 26.2157 | 26.0807 | 26.1857 | 25.4332 | 25.7232 | 25.7232 | 26.2032 | 26.2032 | 26.0457 | 26.4857
2026-05-01 | 22.3567 |  |  |  |  | 2026-08-01 | 2026-09-01 | 25.353 | 25.678 | 25.678 | 25.543 | 25.648 | 24.8955 | 25.1855 | 25.1855 | 25.6655 | 25.6655 | 25.508 | 25.948
2026-06-01 | 23.3554 |  |  |  |  | 2026-09-01 | 2026-10-01 | 22.2799 | 22.6049 | 22.6049 | 22.4699 | 22.5749 | 21.8224 | 22.1124 | 22.1124 | 22.5924 | 22.5924 | 22.4349 | 22.8749
2026-07-01 | 25.8907 |  |  |  |  | 2026-10-01 | 2026-11-01 | 24.7383 | 25.0633 | 25.0633 | 24.9283 | 25.0333 | 24.2808 | 24.5708 | 24.5708 | 25.0508 | 25.0508 | 24.8933 | 25.3333
2026-08-01 | 25.353 |  |  |  |  | 2026-11-01 | 2026-12-01 | 26.0444 | 26.3694 | 26.3694 | 26.2344 | 26.3394 | 25.5869 | 25.8769 | 25.8769 | 26.3569 | 26.3569 | 26.1994 | 26.6394
2026-09-01 | 22.2799 |  |  |  |  | 2026-12-01 | 2027-01-01 | 27.1968 | 27.5218 | 27.5218 | 27.3868 | 27.4918 | 26.7393 | 27.0293 | 27.0293 | 27.5093 | 27.5093 | 27.3518 | 27.7918
2026-10-01 | 24.7383 |  |  |  |  | 2027-01-01 | 2027-02-01 | 40.6427 | 40.9677 | 40.9677 | 40.8327 | 40.9377 | 40.1852 | 40.4752 | 40.4752 | 40.9552 | 40.9552 | 40.7977 | 41.2377
2026-11-01 | 26.0444 |  |  |  |  | 2027-02-01 | 2027-03-01 | 37.0317 | 37.3567 | 37.3567 | 37.2217 | 37.3267 | 36.5742 | 36.8642 | 36.8642 | 37.3442 | 37.3442 | 37.1867 | 37.6267
2026-12-01 | 27.1968 |  |  |  |  | 2027-03-01 | 2027-04-01 | 30.0403 | 30.3653 | 30.3653 | 30.2303 | 30.3353 | 29.5828 | 29.8728 | 29.8728 | 30.3528 | 30.3528 | 30.1953 | 30.6353
2027-01-01 | 40.6427 |  |  |  |  | 2027-04-01 | 2027-05-01 | 28.35 | 28.675 | 28.675 | 28.54 | 28.645 | 27.8925 | 28.1825 | 28.1825 | 28.6625 | 28.6625 | 28.505 | 28.945
2027-02-01 | 37.0317 |  |  |  |  | 2027-05-01 | 2027-06-01 | 22.3573 | 22.6823 | 22.6823 | 22.5473 | 22.6523 | 21.8998 | 22.1898 | 22.1898 | 22.6698 | 22.6698 | 22.5123 | 22.9523
2027-03-01 | 30.0403 |  |  |  |  | 2027-06-01 | 2027-07-01 | 23.3561 | 23.6811 | 23.6811 | 23.5461 | 23.6511 | 22.8986 | 23.1886 | 23.1886 | 23.6686 | 23.6686 | 23.5111 | 23.9511
2027-04-01 | 28.35 |  |  |  |  | 2027-07-01 | 2027-08-01 | 25.8915 | 26.2165 | 26.2165 | 26.0815 | 26.1865 | 25.434 | 25.724 | 25.724 | 26.204 | 26.204 | 26.0465 | 26.4865
2027-05-01 | 22.3573 |  |  |  |  | 2027-08-01 | 2027-09-01 | 25.3537 | 25.6787 | 25.6787 | 25.5437 | 25.6487 | 24.8962 | 25.1862 | 25.1862 | 25.6662 | 25.6662 | 25.5087 | 25.9487
2027-06-01 | 23.3561 |  |  |  |  | 2027-09-01 | 2027-10-01 | 22.2805 | 22.6055 | 22.6055 | 22.4705 | 22.5755 | 21.823 | 22.113 | 22.113 | 22.593 | 22.593 | 22.4355 | 22.8755
2027-07-01 | 25.8915 |  |  |  |  | 2027-10-01 | 2027-11-01 | 24.7391 | 25.0641 | 25.0641 | 24.9291 | 25.0341 | 24.2816 | 24.5716 | 24.5716 | 25.0516 | 25.0516 | 24.8941 | 25.3341
2027-08-01 | 25.3537 |  |  |  |  | 2027-11-01 | 2027-12-01 | 26.0452 | 26.3702 | 26.3702 | 26.2352 | 26.3402 | 25.5877 | 25.8777 | 25.8777 | 26.3577 | 26.3577 | 26.2002 | 26.6402
2027-09-01 | 22.2805 |  |  |  |  | 2027-12-01 | 2028-01-01 | 27.1976 | 27.5226 | 27.5226 | 27.3876 | 27.4926 | 26.7401 | 27.0301 | 27.0301 | 27.5101 | 27.5101 | 27.3526 | 27.7926
2027-10-01 | 24.7391 |  |  |  |  | 2028-01-01 | 2028-02-01 | 41.0719 | 41.3969 | 41.3969 | 41.2619 | 41.3669 | 40.6144 | 40.9044 | 40.9044 | 41.3844 | 41.3844 | 41.2269 | 41.6669
2027-11-01 | 26.0452 |  |  |  |  | 2028-02-01 | 2028-03-01 | 37.4228 | 37.7478 | 37.7478 | 37.6128 | 37.7178 | 36.9653 | 37.2553 | 37.2553 | 37.7353 | 37.7353 | 37.5778 | 38.0178
2027-12-01 | 27.1976 |  |  |  |  | 2028-03-01 | 2028-04-01 | 30.3575 | 30.6825 | 30.6825 | 30.5475 | 30.6525 | 29.9 | 30.19 | 30.19 | 30.67 | 30.67 | 30.5125 | 30.9525
2028-01-01 | 41.0719 |  |  |  |  | 2028-04-01 | 2028-05-01 | 28.6494 | 28.9744 | 28.9744 | 28.8394 | 28.9444 | 28.1919 | 28.4819 | 28.4819 | 28.9619 | 28.9619 | 28.8044 | 29.2444
2028-02-01 | 37.4228 |  |  |  |  | 2028-05-01 | 2028-06-01 | 22.5934 | 22.9184 | 22.9184 | 22.7834 | 22.8884 | 22.1359 | 22.4259 | 22.4259 | 22.9059 | 22.9059 | 22.7484 | 23.1884
2028-03-01 | 30.3575 |  |  |  |  | 2028-06-01 | 2028-07-01 | 23.6027 | 23.9277 | 23.9277 | 23.7927 | 23.8977 | 23.1452 | 23.4352 | 23.4352 | 23.9152 | 23.9152 | 23.7577 | 24.1977
2028-04-01 | 28.6494 |  |  |  |  | 2028-07-01 | 2028-08-01 | 26.1649 | 26.4899 | 26.4899 | 26.3549 | 26.4599 | 25.7074 | 25.9974 | 25.9974 | 26.4774 | 26.4774 | 26.3199 | 26.7599
2028-05-01 | 22.5934 |  |  |  |  | 2028-08-01 | 2028-09-01 | 25.6214 | 25.9464 | 25.9464 | 25.8114 | 25.9164 | 25.1639 | 25.4539 | 25.4539 | 25.9339 | 25.9339 | 25.7764 | 26.2164
2028-06-01 | 23.6027 |  |  |  |  | 2028-09-01 | 2028-10-01 | 22.5158 | 22.8408 | 22.8408 | 22.7058 | 22.8108 | 22.0583 | 22.3483 | 22.3483 | 22.8283 | 22.8283 | 22.6708 | 23.1108
2028-07-01 | 26.1649 |  |  |  |  | 2028-10-01 | 2028-11-01 | 25.0003 | 25.3253 | 25.3253 | 25.1903 | 25.2953 | 24.5428 | 24.8328 | 24.8328 | 25.3128 | 25.3128 | 25.1553 | 25.5953
2028-08-01 | 25.6214 |  |  |  |  | 2028-11-01 | 2028-12-01 | 26.3202 | 26.6452 | 26.6452 | 26.5102 | 26.6152 | 25.8627 | 26.1527 | 26.1527 | 26.6327 | 26.6327 | 26.4752 | 26.9152
2028-09-01 | 22.5158 |  |  |  |  | 2028-12-01 | 2029-01-01 | 27.4848 | 27.8098 | 27.8098 | 27.6748 | 27.7798 | 27.0273 | 27.3173 | 27.3173 | 27.7973 | 27.7973 | 27.6398 | 28.0798
2028-10-01 | 25.0003 |  |  |  |  | 2029-01-01 | 2029-02-01 | 41.5211 | 41.8461 | 41.8461 | 41.7111 | 41.8161 | 41.0636 | 41.3536 | 41.3536 | 41.8336 | 41.8336 | 41.6761 | 42.1161
2028-11-01 | 26.3202 |  |  |  |  | 2029-02-01 | 2029-03-01 | 37.8321 | 38.1571 | 38.1571 | 38.0221 | 38.1271 | 37.3746 | 37.6646 | 37.6646 | 38.1446 | 38.1446 | 37.9871 | 38.4271
2028-12-01 | 27.4848 |  |  |  |  | 2029-03-01 | 2029-04-01 | 30.6895 | 31.0145 | 31.0145 | 30.8795 | 30.9845 | 30.232 | 30.522 | 30.522 | 31.002 | 31.002 | 30.8445 | 31.2845
2029-01-01 | 41.5211 |  |  |  |  | 2029-04-01 | 2029-05-01 | 28.9627 | 29.2877 | 29.2877 | 29.1527 | 29.2577 | 28.5052 | 28.7952 | 28.7952 | 29.2752 | 29.2752 | 29.1177 | 29.5577
2029-02-01 | 37.8321 |  |  |  |  | 2029-05-01 | 2029-06-01 | 22.8405 | 23.1655 | 23.1655 | 23.0305 | 23.1355 | 22.383 | 22.673 | 22.673 | 23.153 | 23.153 | 22.9955 | 23.4355
2029-03-01 | 30.6895 |  |  |  |  | 2029-06-01 | 2029-07-01 | 23.8609 | 24.1859 | 24.1859 | 24.0509 | 24.1559 | 23.4034 | 23.6934 | 23.6934 | 24.1734 | 24.1734 | 24.0159 | 24.4559
2029-04-01 | 28.9627 |  |  |  |  | 2029-07-01 | 2029-08-01 | 26.4511 | 26.7761 | 26.7761 | 26.6411 | 26.7461 | 25.9936 | 26.2836 | 26.2836 | 26.7636 | 26.7636 | 26.6061 | 27.0461
2029-05-01 | 22.8405 |  |  |  |  | 2029-08-01 | 2029-09-01 | 25.9016 | 26.2266 | 26.2266 | 26.0916 | 26.1966 | 25.4441 | 25.7341 | 25.7341 | 26.2141 | 26.2141 | 26.0566 | 26.4966
2029-06-01 | 23.8609 |  |  |  |  | 2029-09-01 | 2029-10-01 | 22.762 | 23.087 | 23.087 | 22.952 | 23.057 | 22.3045 | 22.5945 | 22.5945 | 23.0745 | 23.0745 | 22.917 | 23.357
2029-07-01 | 26.4511 |  |  |  |  | 2029-10-01 | 2029-11-01 | 25.2737 | 25.5987 | 25.5987 | 25.4637 | 25.5687 | 24.8162 | 25.1062 | 25.1062 | 25.5862 | 25.5862 | 25.4287 | 25.8687
2029-08-01 | 25.9016 |  |  |  |  | 2029-11-01 | 2029-12-01 | 26.608 | 26.933 | 26.933 | 26.798 | 26.903 | 26.1505 | 26.4405 | 26.4405 | 26.9205 | 26.9205 | 26.763 | 27.203
2029-09-01 | 22.762 |  |  |  |  | 2029-12-01 | 2030-01-01 | 27.7854 | 28.1104 | 28.1104 | 27.9754 | 28.0804 | 27.3279 | 27.6179 | 27.6179 | 28.0979 | 28.0979 | 27.9404 | 28.3804
2029-10-01 | 25.2737 |  |  |  |  | 2030-01-01 | 2030-02-01 | 42.2247 | 42.5497 | 42.5497 | 42.4147 | 42.5197 | 41.7672 | 42.0572 | 42.0572 | 42.5372 | 42.5372 | 42.3797 | 42.8197
2029-11-01 | 26.608 |  |  |  |  | 2030-02-01 | 2030-03-01 | 38.4731 | 38.7981 | 38.7981 | 38.6631 | 38.7681 | 38.0156 | 38.3056 | 38.3056 | 38.7856 | 38.7856 | 38.6281 | 39.0681
2029-12-01 | 27.7854 |  |  |  |  | 2030-03-01 | 2030-04-01 | 31.2095 | 31.5345 | 31.5345 | 31.3995 | 31.5045 | 30.752 | 31.042 | 31.042 | 31.522 | 31.522 | 31.3645 | 31.8045
2030-01-01 | 42.2247 |  |  |  |  | 2030-04-01 | 2030-05-01 | 29.4535 | 29.7785 | 29.7785 | 29.6435 | 29.7485 | 28.996 | 29.286 | 29.286 | 29.766 | 29.766 | 29.6085 | 30.0485
2030-02-01 | 38.4731 |  |  |  |  | 2030-05-01 | 2030-06-01 | 23.2276 | 23.5526 | 23.5526 | 23.4176 | 23.5226 | 22.7701 | 23.0601 | 23.0601 | 23.5401 | 23.5401 | 23.3826 | 23.8226
2030-03-01 | 31.2095 |  |  |  |  | 2030-06-01 | 2030-07-01 | 24.2652 | 24.5902 | 24.5902 | 24.4552 | 24.5602 | 23.8077 | 24.0977 | 24.0977 | 24.5777 | 24.5777 | 24.4202 | 24.8602
2030-04-01 | 29.4535 |  |  |  |  | 2030-07-01 | 2030-08-01 | 26.8993 | 27.2243 | 27.2243 | 27.0893 | 27.1943 | 26.4418 | 26.7318 | 26.7318 | 27.2118 | 27.2118 | 27.0543 | 27.4943
2030-05-01 | 23.2276 |  |  |  |  | 2030-08-01 | 2030-09-01 | 26.3405 | 26.6655 | 26.6655 | 26.5305 | 26.6355 | 25.883 | 26.173 | 26.173 | 26.653 | 26.653 | 26.4955 | 26.9355
2030-06-01 | 24.2652 |  |  |  |  | 2030-09-01 | 2030-10-01 | 23.1477 | 23.4727 | 23.4727 | 23.3377 | 23.4427 | 22.6902 | 22.9802 | 22.9802 | 23.4602 | 23.4602 | 23.3027 | 23.7427
2030-07-01 | 26.8993 |  |  |  |  | 2030-10-01 | 2030-11-01 | 25.702 | 26.027 | 26.027 | 25.892 | 25.997 | 25.2445 | 25.5345 | 25.5345 | 26.0145 | 26.0145 | 25.857 | 26.297
2030-08-01 | 26.3405 |  |  |  |  | 2030-11-01 | 2030-12-01 | 27.0589 | 27.3839 | 27.3839 | 27.2489 | 27.3539 | 26.6014 | 26.8914 | 26.8914 | 27.3714 | 27.3714 | 27.2139 | 27.6539
2030-09-01 | 23.1477 |  |  |  |  | 2030-12-01 | 2031-01-01 | 28.2562 | 28.5812 | 28.5812 | 28.4462 | 28.5512 | 27.7987 | 28.0887 | 28.0887 | 28.5687 | 28.5687 | 28.4112 | 28.8512
2030-10-01 | 25.702 |  |  |  |  | 2031-01-01 | 2031-02-01 | 43.3167 | 43.6417 | 43.6417 | 43.5067 | 43.6117 | 42.8592 | 43.1492 | 43.1492 | 43.6292 | 43.6292 | 43.4717 | 43.9117
2030-11-01 | 27.0589 |  |  |  |  | 2031-02-01 | 2031-03-01 | 39.4682 | 39.7932 | 39.7932 | 39.6582 | 39.7632 | 39.0107 | 39.3007 | 39.3007 | 39.7807 | 39.7807 | 39.6232 | 40.0632
2030-12-01 | 28.2562 |  |  |  |  | 2031-03-01 | 2031-04-01 | 32.0167 | 32.3417 | 32.3417 | 32.2067 | 32.3117 | 31.5592 | 31.8492 | 31.8492 | 32.3292 | 32.3292 | 32.1717 | 32.6117
2031-01-01 | 43.3167 |  |  |  |  | 2031-04-01 | 2031-05-01 | 30.2153 | 30.5403 | 30.5403 | 30.4053 | 30.5103 | 29.7578 | 30.0478 | 30.0478 | 30.5278 | 30.5278 | 30.3703 | 30.8103
2031-02-01 | 39.4682 |  |  |  |  | 2031-05-01 | 2031-06-01 | 23.8283 | 24.1533 | 24.1533 | 24.0183 | 24.1233 | 23.3708 | 23.6608 | 23.6608 | 24.1408 | 24.1408 | 23.9833 | 24.4233
2031-03-01 | 32.0167 |  |  |  |  | 2031-06-01 | 2031-07-01 | 24.8928 | 25.2178 | 25.2178 | 25.0828 | 25.1878 | 24.4353 | 24.7253 | 24.7253 | 25.2053 | 25.2053 | 25.0478 | 25.4878
2031-04-01 | 30.2153 |  |  |  |  | 2031-07-01 | 2031-08-01 | 27.595 | 27.92 | 27.92 | 27.785 | 27.89 | 27.1375 | 27.4275 | 27.4275 | 27.9075 | 27.9075 | 27.75 | 28.19
2031-05-01 | 23.8283 |  |  |  |  | 2031-08-01 | 2031-09-01 | 27.0218 | 27.3468 | 27.3468 | 27.2118 | 27.3168 | 26.5643 | 26.8543 | 26.8543 | 27.3343 | 27.3343 | 27.1768 | 27.6168
2031-06-01 | 24.8928 |  |  |  |  | 2031-09-01 | 2031-10-01 | 23.7464 | 24.0714 | 24.0714 | 23.9364 | 24.0414 | 23.2889 | 23.5789 | 23.5789 | 24.0589 | 24.0589 | 23.9014 | 24.3414
2031-07-01 | 27.595 |  |  |  |  | 2031-10-01 | 2031-11-01 | 26.3667 | 26.6917 | 26.6917 | 26.5567 | 26.6617 | 25.9092 | 26.1992 | 26.1992 | 26.6792 | 26.6792 | 26.5217 | 26.9617
2031-08-01 | 27.0218 |  |  |  |  | 2031-11-01 | 2031-12-01 | 27.7587 | 28.0837 | 28.0837 | 27.9487 | 28.0537 | 27.3012 | 27.5912 | 27.5912 | 28.0712 | 28.0712 | 27.9137 | 28.3537
2031-09-01 | 23.7464 |  |  |  |  | 2031-12-01 | 2032-01-01 | 28.987 | 29.312 | 29.312 | 29.177 | 29.282 | 28.5295 | 28.8195 | 28.8195 | 29.2995 | 29.2995 | 29.142 | 29.582
2031-10-01 | 26.3667 |  |  |  |  | 2032-01-01 | 2032-02-01 | 45.2732 | 45.5982 | 45.5982 | 45.4632 | 45.5682 | 44.8157 | 45.1057 | 45.1057 | 45.5857 | 45.5857 | 45.4282 | 45.8682
2031-11-01 | 27.7587 |  |  |  |  | 2032-02-01 | 2032-03-01 | 41.2509 | 41.5759 | 41.5759 | 41.4409 | 41.5459 | 40.7934 | 41.0834 | 41.0834 | 41.5634 | 41.5634 | 41.4059 | 41.8459
2031-12-01 | 28.987 |  |  |  |  | 2032-03-01 | 2032-04-01 | 33.4628 | 33.7878 | 33.7878 | 33.6528 | 33.7578 | 33.0053 | 33.2953 | 33.2953 | 33.7753 | 33.7753 | 33.6178 | 34.0578
2032-01-01 | 45.2732 |  |  |  |  | 2032-04-01 | 2032-05-01 | 31.58 | 31.905 | 31.905 | 31.77 | 31.875 | 31.1225 | 31.4125 | 31.4125 | 31.8925 | 31.8925 | 31.735 | 32.175
2032-02-01 | 41.2509 |  |  |  |  | 2032-05-01 | 2032-06-01 | 24.9046 | 25.2296 | 25.2296 | 25.0946 | 25.1996 | 24.4471 | 24.7371 | 24.7371 | 25.2171 | 25.2171 | 25.0596 | 25.4996
2032-03-01 | 33.4628 |  |  |  |  | 2032-06-01 | 2032-07-01 | 26.0171 | 26.3421 | 26.3421 | 26.2071 | 26.3121 | 25.5596 | 25.8496 | 25.8496 | 26.3296 | 26.3296 | 26.1721 | 26.6121
2032-04-01 | 31.58 |  |  |  |  | 2032-07-01 | 2032-08-01 | 28.8414 | 29.1664 | 29.1664 | 29.0314 | 29.1364 | 28.3839 | 28.6739 | 28.6739 | 29.1539 | 29.1539 | 28.9964 | 29.4364
2032-05-01 | 24.9046 |  |  |  |  | 2032-08-01 | 2032-09-01 | 28.2423 | 28.5673 | 28.5673 | 28.4323 | 28.5373 | 27.7848 | 28.0748 | 28.0748 | 28.5548 | 28.5548 | 28.3973 | 28.8373
2032-06-01 | 26.0171 |  |  |  |  | 2032-09-01 | 2032-10-01 | 24.819 | 25.144 | 25.144 | 25.009 | 25.114 | 24.3615 | 24.6515 | 24.6515 | 25.1315 | 25.1315 | 24.974 | 25.414
2032-07-01 | 28.8414 |  |  |  |  | 2032-10-01 | 2032-11-01 | 27.5576 | 27.8826 | 27.8826 | 27.7476 | 27.8526 | 27.1001 | 27.3901 | 27.3901 | 27.8701 | 27.8701 | 27.7126 | 28.1526
2032-08-01 | 28.2423 |  |  |  |  | 2032-11-01 | 2032-12-01 | 29.0125 | 29.3375 | 29.3375 | 29.2025 | 29.3075 | 28.555 | 28.845 | 28.845 | 29.325 | 29.325 | 29.1675 | 29.6075
2032-09-01 | 24.819 |  |  |  |  | 2032-12-01 | 2033-01-01 | 30.2963 | 30.6213 | 30.6213 | 30.4863 | 30.5913 | 29.8388 | 30.1288 | 30.1288 | 30.6088 | 30.6088 | 30.4513 | 30.8913
2032-10-01 | 27.5576 |  |  |  |  | 2033-01-01 | 2033-02-01 | 46.7146 | 47.0396 | 47.0396 | 46.9046 | 47.0096 | 46.2571 | 46.5471 | 46.5471 | 47.0271 | 47.0271 | 46.8696 | 47.3096
2032-11-01 | 29.0125 |  |  |  |  | 2033-02-01 | 2033-03-01 | 42.5641 | 42.8891 | 42.8891 | 42.7541 | 42.8591 | 42.1066 | 42.3966 | 42.3966 | 42.8766 | 42.8766 | 42.7191 | 43.1591
2032-12-01 | 30.2963 |  |  |  |  | 2033-03-01 | 2033-04-01 | 34.5282 | 34.8532 | 34.8532 | 34.7182 | 34.8232 | 34.0707 | 34.3607 | 34.3607 | 34.8407 | 34.8407 | 34.6832 | 35.1232
2033-01-01 | 46.7146 |  |  |  |  | 2033-04-01 | 2033-05-01 | 32.5854 | 32.9104 | 32.9104 | 32.7754 | 32.8804 | 32.1279 | 32.4179 | 32.4179 | 32.8979 | 32.8979 | 32.7404 | 33.1804
2033-02-01 | 42.5641 |  |  |  |  | 2033-05-01 | 2033-06-01 | 25.6974 | 26.0224 | 26.0224 | 25.8874 | 25.9924 | 25.2399 | 25.5299 | 25.5299 | 26.0099 | 26.0099 | 25.8524 | 26.2924
2033-03-01 | 34.5282 |  |  |  |  | 2033-06-01 | 2033-07-01 | 26.8454 | 27.1704 | 27.1704 | 27.0354 | 27.1404 | 26.3879 | 26.6779 | 26.6779 | 27.1579 | 27.1579 | 27.0004 | 27.4404
2033-04-01 | 32.5854 |  |  |  |  | 2033-07-01 | 2033-08-01 | 29.7596 | 30.0846 | 30.0846 | 29.9496 | 30.0546 | 29.3021 | 29.5921 | 29.5921 | 30.0721 | 30.0721 | 29.9146 | 30.3546
2033-05-01 | 25.6974 |  |  |  |  | 2033-08-01 | 2033-09-01 | 29.1414 | 29.4664 | 29.4664 | 29.3314 | 29.4364 | 28.6839 | 28.9739 | 28.9739 | 29.4539 | 29.4539 | 29.2964 | 29.7364
2033-06-01 | 26.8454 |  |  |  |  | 2033-09-01 | 2033-10-01 | 25.6091 | 25.9341 | 25.9341 | 25.7991 | 25.9041 | 25.1516 | 25.4416 | 25.4416 | 25.9216 | 25.9216 | 25.7641 | 26.2041
2033-07-01 | 29.7596 |  |  |  |  | 2033-10-01 | 2033-11-01 | 28.435 | 28.76 | 28.76 | 28.625 | 28.73 | 27.9775 | 28.2675 | 28.2675 | 28.7475 | 28.7475 | 28.59 | 29.03
2033-08-01 | 29.1414 |  |  |  |  | 2033-11-01 | 2033-12-01 | 29.9362 | 30.2612 | 30.2612 | 30.1262 | 30.2312 | 29.4787 | 29.7687 | 29.7687 | 30.2487 | 30.2487 | 30.0912 | 30.5312
2033-09-01 | 25.6091 |  |  |  |  | 2033-12-01 | 2034-01-01 | 31.2608 | 31.5858 | 31.5858 | 31.4508 | 31.5558 | 30.8033 | 31.0933 | 31.0933 | 31.5733 | 31.5733 | 31.4158 | 31.8558
2033-10-01 | 28.435 |  |  |  |  | 2034-01-01 | 2034-02-01 | 48.1747 | 48.4997 | 48.4997 | 48.3647 | 48.4697 | 47.7172 | 48.0072 | 48.0072 | 48.4872 | 48.4872 | 48.3297 | 48.7697
2033-11-01 | 29.9362 |  |  |  |  | 2034-02-01 | 2034-03-01 | 43.8946 | 44.2196 | 44.2196 | 44.0846 | 44.1896 | 43.4371 | 43.7271 | 43.7271 | 44.2071 | 44.2071 | 44.0496 | 44.4896
2033-12-01 | 31.2608 |  |  |  |  | 2034-03-01 | 2034-04-01 | 35.6074 | 35.9324 | 35.9324 | 35.7974 | 35.9024 | 35.1499 | 35.4399 | 35.4399 | 35.9199 | 35.9199 | 35.7624 | 36.2024
2034-01-01 | 48.1747 |  |  |  |  | 2034-04-01 | 2034-05-01 | 33.6039 | 33.9289 | 33.9289 | 33.7939 | 33.8989 | 33.1464 | 33.4364 | 33.4364 | 33.9164 | 33.9164 | 33.7589 | 34.1989
2034-02-01 | 43.8946 |  |  |  |  | 2034-05-01 | 2034-06-01 | 26.5007 | 26.8257 | 26.8257 | 26.6907 | 26.7957 | 26.0432 | 26.3332 | 26.3332 | 26.8132 | 26.8132 | 26.6557 | 27.0957
2034-03-01 | 35.6074 |  |  |  |  | 2034-06-01 | 2034-07-01 | 27.6845 | 28.0095 | 28.0095 | 27.8745 | 27.9795 | 27.227 | 27.517 | 27.517 | 27.997 | 27.997 | 27.8395 | 28.2795
2034-04-01 | 33.6039 |  |  |  |  | 2034-07-01 | 2034-08-01 | 30.6898 | 31.0148 | 31.0148 | 30.8798 | 30.9848 | 30.2323 | 30.5223 | 30.5223 | 31.0023 | 31.0023 | 30.8448 | 31.2848
2034-05-01 | 26.5007 |  |  |  |  | 2034-08-01 | 2034-09-01 | 30.0523 | 30.3773 | 30.3773 | 30.2423 | 30.3473 | 29.5948 | 29.8848 | 29.8848 | 30.3648 | 30.3648 | 30.2073 | 30.6473
2034-06-01 | 27.6845 |  |  |  |  | 2034-09-01 | 2034-10-01 | 26.4096 | 26.7346 | 26.7346 | 26.5996 | 26.7046 | 25.9521 | 26.2421 | 26.2421 | 26.7221 | 26.7221 | 26.5646 | 27.0046
2034-07-01 | 30.6898 |  |  |  |  | 2034-10-01 | 2034-11-01 | 29.3238 | 29.6488 | 29.6488 | 29.5138 | 29.6188 | 28.8663 | 29.1563 | 29.1563 | 29.6363 | 29.6363 | 29.4788 | 29.9188
2034-08-01 | 30.0523 |  |  |  |  | 2034-11-01 | 2034-12-01 | 30.8719 | 31.1969 | 31.1969 | 31.0619 | 31.1669 | 30.4144 | 30.7044 | 30.7044 | 31.1844 | 31.1844 | 31.0269 | 31.4669
2034-09-01 | 26.4096 |  |  |  |  | 2034-12-01 | 2035-01-01 | 32.2379 | 32.5629 | 32.5629 | 32.4279 | 32.5329 | 31.7804 | 32.0704 | 32.0704 | 32.5504 | 32.5504 | 32.3929 | 32.8329
2034-10-01 | 29.3238 |  |  |  |  | 2035-01-01 | 2035-02-01 | 49.2377 | 49.5627 | 49.5627 | 49.4277 | 49.5327 | 48.7802 | 49.0702 | 49.0702 | 49.5502 | 49.5502 | 49.3927 | 49.8327
2034-11-01 | 30.8719 |  |  |  |  | 2035-02-01 | 2035-03-01 | 44.8631 | 45.1881 | 45.1881 | 45.0531 | 45.1581 | 44.4056 | 44.6956 | 44.6956 | 45.1756 | 45.1756 | 45.0181 | 45.4581
2034-12-01 | 32.2379 |  |  |  |  | 2035-03-01 | 2035-04-01 | 36.3931 | 36.7181 | 36.7181 | 36.5831 | 36.6881 | 35.9356 | 36.2256 | 36.2256 | 36.7056 | 36.7056 | 36.5481 | 36.9881
2035-01-01 | 49.2377 |  |  |  |  | 2035-04-01 | 2035-05-01 | 34.3454 | 34.6704 | 34.6704 | 34.5354 | 34.6404 | 33.8879 | 34.1779 | 34.1779 | 34.6579 | 34.6579 | 34.5004 | 34.9404
2035-02-01 | 44.8631 |  |  |  |  | 2035-05-01 | 2035-06-01 | 27.0854 | 27.4104 | 27.4104 | 27.2754 | 27.3804 | 26.6279 | 26.9179 | 26.9179 | 27.3979 | 27.3979 | 27.2404 | 27.6804
2035-03-01 | 36.3931 |  |  |  |  | 2035-06-01 | 2035-07-01 | 28.2954 | 28.6204 | 28.6204 | 28.4854 | 28.5904 | 27.8379 | 28.1279 | 28.1279 | 28.6079 | 28.6079 | 28.4504 | 28.8904
2035-04-01 | 34.3454 |  |  |  |  | 2035-07-01 | 2035-08-01 | 31.3669 | 31.6919 | 31.6919 | 31.5569 | 31.6619 | 30.9094 | 31.1994 | 31.1994 | 31.6794 | 31.6794 | 31.5219 | 31.9619
2035-05-01 | 27.0854 |  |  |  |  | 2035-08-01 | 2035-09-01 | 30.7154 | 31.0404 | 31.0404 | 30.9054 | 31.0104 | 30.2579 | 30.5479 | 30.5479 | 31.0279 | 31.0279 | 30.8704 | 31.3104
2035-06-01 | 28.2954 |  |  |  |  | 2035-09-01 | 2035-10-01 | 26.9923 | 27.3173 | 27.3173 | 27.1823 | 27.2873 | 26.5348 | 26.8248 | 26.8248 | 27.3048 | 27.3048 | 27.1473 | 27.5873
2035-07-01 | 31.3669 |  |  |  |  | 2035-10-01 | 2035-11-01 | 29.9708 | 30.2958 | 30.2958 | 30.1608 | 30.2658 | 29.5133 | 29.8033 | 29.8033 | 30.2833 | 30.2833 | 30.1258 | 30.5658
2035-08-01 | 30.7154 |  |  |  |  | 2035-11-01 | 2035-12-01 | 31.5531 | 31.8781 | 31.8781 | 31.7431 | 31.8481 | 31.0956 | 31.3856 | 31.3856 | 31.8656 | 31.8656 | 31.7081 | 32.1481
2035-09-01 | 26.9923 |  |  |  |  | 2035-12-01 | 2036-01-01 | 32.9492 | 33.2742 | 33.2742 | 33.1392 | 33.2442 | 32.4917 | 32.7817 | 32.7817 | 33.2617 | 33.2617 | 33.1042 | 33.5442
2035-10-01 | 29.9708 |  |  |  |  | 2036-01-01 | 2036-02-01 | 49.6352 | 49.9602 | 49.9602 | 49.8252 | 49.9302 | 49.1777 | 49.4677 | 49.4677 | 49.9477 | 49.9477 | 49.7902 | 50.2302
2035-11-01 | 31.5531 |  |  |  |  | 2036-02-01 | 2036-03-01 | 45.2253 | 45.5503 | 45.5503 | 45.4153 | 45.5203 | 44.7678 | 45.0578 | 45.0578 | 45.5378 | 45.5378 | 45.3803 | 45.8203
2035-12-01 | 32.9492 |  |  |  |  | 2036-03-01 | 2036-04-01 | 36.6869 | 37.0119 | 37.0119 | 36.8769 | 36.9819 | 36.2294 | 36.5194 | 36.5194 | 36.9994 | 36.9994 | 36.8419 | 37.2819
2036-01-01 | 49.6352 |  |  |  |  | 2036-04-01 | 2036-05-01 | 34.6227 | 34.9477 | 34.9477 | 34.8127 | 34.9177 | 34.1652 | 34.4552 | 34.4552 | 34.9352 | 34.9352 | 34.7777 | 35.2177
2036-02-01 | 45.2253 |  |  |  |  | 2036-05-01 | 2036-06-01 | 27.3041 | 27.6291 | 27.6291 | 27.4941 | 27.5991 | 26.8466 | 27.1366 | 27.1366 | 27.6166 | 27.6166 | 27.4591 | 27.8991
2036-03-01 | 36.6869 |  |  |  |  | 2036-06-01 | 2036-07-01 | 28.5238 | 28.8488 | 28.8488 | 28.7138 | 28.8188 | 28.0663 | 28.3563 | 28.3563 | 28.8363 | 28.8363 | 28.6788 | 29.1188
2036-04-01 | 34.6227 |  |  |  |  | 2036-07-01 | 2036-08-01 | 31.6202 | 31.9452 | 31.9452 | 31.8102 | 31.9152 | 31.1627 | 31.4527 | 31.4527 | 31.9327 | 31.9327 | 31.7752 | 32.2152
2036-05-01 | 27.3041 |  |  |  |  | 2036-08-01 | 2036-09-01 | 30.9634 | 31.2884 | 31.2884 | 31.1534 | 31.2584 | 30.5059 | 30.7959 | 30.7959 | 31.2759 | 31.2759 | 31.1184 | 31.5584
2036-06-01 | 28.5238 |  |  |  |  | 2036-09-01 | 2036-10-01 | 27.2102 | 27.5352 | 27.5352 | 27.4002 | 27.5052 | 26.7527 | 27.0427 | 27.0427 | 27.5227 | 27.5227 | 27.3652 | 27.8052
2036-07-01 | 31.6202 |  |  |  |  | 2036-10-01 | 2036-11-01 | 30.2127 | 30.5377 | 30.5377 | 30.4027 | 30.5077 | 29.7552 | 30.0452 | 30.0452 | 30.5252 | 30.5252 | 30.3677 | 30.8077
2036-08-01 | 30.9634 |  |  |  |  | 2036-11-01 | 2036-12-01 | 31.8078 | 32.1328 | 32.1328 | 31.9978 | 32.1028 | 31.3503 | 31.6403 | 31.6403 | 32.1203 | 32.1203 | 31.9628 | 32.4028
2036-09-01 | 27.2102 |  |  |  |  | 2036-12-01 | 2037-01-01 | 33.2152 | 33.5402 | 33.5402 | 33.4052 | 33.5102 | 32.7577 | 33.0477 | 33.0477 | 33.5277 | 33.5277 | 33.3702 | 33.8102
2036-10-01 | 30.2127 |  |  |  |  | 2037-01-01 | 2037-02-01 | 50.9151 | 51.2401 | 51.2401 | 51.1051 | 51.2101 | 50.4576 | 50.7476 | 50.7476 | 51.2276 | 51.2276 | 51.0701 | 51.5101
2036-11-01 | 31.8078 |  |  |  |  | 2037-02-01 | 2037-03-01 | 46.3914 | 46.7164 | 46.7164 | 46.5814 | 46.6864 | 45.9339 | 46.2239 | 46.2239 | 46.7039 | 46.7039 | 46.5464 | 46.9864
2036-12-01 | 33.2152 |  |  |  |  | 2037-03-01 | 2037-04-01 | 37.6329 | 37.9579 | 37.9579 | 37.8229 | 37.9279 | 37.1754 | 37.4654 | 37.4654 | 37.9454 | 37.9454 | 37.7879 | 38.2279
2037-01-01 | 50.9151 |  |  |  |  | 2037-04-01 | 2037-05-01 | 35.5154 | 35.8404 | 35.8404 | 35.7054 | 35.8104 | 35.0579 | 35.3479 | 35.3479 | 35.8279 | 35.8279 | 35.6704 | 36.1104
2037-02-01 | 46.3914 |  |  |  |  | 2037-05-01 | 2037-06-01 | 28.0081 | 28.3331 | 28.3331 | 28.1981 | 28.3031 | 27.5506 | 27.8406 | 27.8406 | 28.3206 | 28.3206 | 28.1631 | 28.6031
2037-03-01 | 37.6329 |  |  |  |  | 2037-06-01 | 2037-07-01 | 29.2593 | 29.5843 | 29.5843 | 29.4493 | 29.5543 | 28.8018 | 29.0918 | 29.0918 | 29.5718 | 29.5718 | 29.4143 | 29.8543
2037-04-01 | 35.5154 |  |  |  |  | 2037-07-01 | 2037-08-01 | 32.4355 | 32.7605 | 32.7605 | 32.6255 | 32.7305 | 31.978 | 32.268 | 32.268 | 32.748 | 32.748 | 32.5905 | 33.0305
2037-05-01 | 28.0081 |  |  |  |  | 2037-08-01 | 2037-09-01 | 31.7618 | 32.0868 | 32.0868 | 31.9518 | 32.0568 | 31.3043 | 31.5943 | 31.5943 | 32.0743 | 32.0743 | 31.9168 | 32.3568
2037-06-01 | 29.2593 |  |  |  |  | 2037-09-01 | 2037-10-01 | 27.9118 | 28.2368 | 28.2368 | 28.1018 | 28.2068 | 27.4543 | 27.7443 | 27.7443 | 28.2243 | 28.2243 | 28.0668 | 28.5068
2037-07-01 | 32.4355 |  |  |  |  | 2037-10-01 | 2037-11-01 | 30.9918 | 31.3168 | 31.3168 | 31.1818 | 31.2868 | 30.5343 | 30.8243 | 30.8243 | 31.3043 | 31.3043 | 31.1468 | 31.5868
2037-08-01 | 31.7618 |  |  |  |  | 2037-11-01 | 2037-12-01 | 32.628 | 32.953 | 32.953 | 32.818 | 32.923 | 32.1705 | 32.4605 | 32.4605 | 32.9405 | 32.9405 | 32.783 | 33.223
2037-09-01 | 27.9118 |  |  |  |  | 2037-12-01 | 2038-01-01 | 34.0717 | 34.3967 | 34.3967 | 34.2617 | 34.3667 | 33.6142 | 33.9042 | 33.9042 | 34.3842 | 34.3842 | 34.2267 | 34.6667
2037-10-01 | 30.9918 |  |  |  |  | 2038-01-01 | 2038-02-01 | 52.266 | 52.591 | 52.591 | 52.456 | 52.561 | 51.8085 | 52.0985 | 52.0985 | 52.5785 | 52.5785 | 52.421 | 52.861
2037-11-01 | 32.628 |  |  |  |  | 2038-02-01 | 2038-03-01 | 47.6223 | 47.9473 | 47.9473 | 47.8123 | 47.9173 | 47.1648 | 47.4548 | 47.4548 | 47.9348 | 47.9348 | 47.7773 | 48.2173
2037-12-01 | 34.0717 |  |  |  |  | 2038-03-01 | 2038-04-01 | 38.6314 | 38.9564 | 38.9564 | 38.8214 | 38.9264 | 38.1739 | 38.4639 | 38.4639 | 38.9439 | 38.9439 | 38.7864 | 39.2264
2038-01-01 | 52.266 |  |  |  |  | 2038-04-01 | 2038-05-01 | 36.4577 | 36.7827 | 36.7827 | 36.6477 | 36.7527 | 36.0002 | 36.2902 | 36.2902 | 36.7702 | 36.7702 | 36.6127 | 37.0527
2038-02-01 | 47.6223 |  |  |  |  | 2038-05-01 | 2038-06-01 | 28.7512 | 29.0762 | 29.0762 | 28.9412 | 29.0462 | 28.2937 | 28.5837 | 28.5837 | 29.0637 | 29.0637 | 28.9062 | 29.3462
2038-03-01 | 38.6314 |  |  |  |  | 2038-06-01 | 2038-07-01 | 30.0357 | 30.3607 | 30.3607 | 30.2257 | 30.3307 | 29.5782 | 29.8682 | 29.8682 | 30.3482 | 30.3482 | 30.1907 | 30.6307
2038-04-01 | 36.4577 |  |  |  |  | 2038-07-01 | 2038-08-01 | 33.2961 | 33.6211 | 33.6211 | 33.4861 | 33.5911 | 32.8386 | 33.1286 | 33.1286 | 33.6086 | 33.6086 | 33.4511 | 33.8911
2038-05-01 | 28.7512 |  |  |  |  | 2038-08-01 | 2038-09-01 | 32.6045 | 32.9295 | 32.9295 | 32.7945 | 32.8995 | 32.147 | 32.437 | 32.437 | 32.917 | 32.917 | 32.7595 | 33.1995
2038-06-01 | 30.0357 |  |  |  |  | 2038-09-01 | 2038-10-01 | 28.6524 | 28.9774 | 28.9774 | 28.8424 | 28.9474 | 28.1949 | 28.4849 | 28.4849 | 28.9649 | 28.9649 | 28.8074 | 29.2474
2038-07-01 | 33.2961 |  |  |  |  | 2038-10-01 | 2038-11-01 | 31.8141 | 32.1391 | 32.1391 | 32.0041 | 32.1091 | 31.3566 | 31.6466 | 31.6466 | 32.1266 | 32.1266 | 31.9691 | 32.4091
2038-08-01 | 32.6045 |  |  |  |  | 2038-11-01 | 2038-12-01 | 33.4937 | 33.8187 | 33.8187 | 33.6837 | 33.7887 | 33.0362 | 33.3262 | 33.3262 | 33.8062 | 33.8062 | 33.6487 | 34.0887
2038-09-01 | 28.6524 |  |  |  |  | 2038-12-01 | 2039-01-01 | 34.9757 | 35.3007 | 35.3007 | 35.1657 | 35.2707 | 34.5182 | 34.8082 | 34.8082 | 35.2882 | 35.2882 | 35.1307 | 35.5707
2038-10-01 | 31.8141 |  |  |  |  | 2039-01-01 | 2039-02-01 | 53.4601 | 53.7851 | 53.7851 | 53.6501 | 53.7551 | 53.0026 | 53.2926 | 53.2926 | 53.7726 | 53.7726 | 53.6151 | 54.0551
2038-11-01 | 33.4937 |  |  |  |  | 2039-02-01 | 2039-03-01 | 48.7104 | 49.0354 | 49.0354 | 48.9004 | 49.0054 | 48.2529 | 48.5429 | 48.5429 | 49.0229 | 49.0229 | 48.8654 | 49.3054
2038-12-01 | 34.9757 |  |  |  |  | 2039-03-01 | 2039-04-01 | 39.514 | 39.839 | 39.839 | 39.704 | 39.809 | 39.0565 | 39.3465 | 39.3465 | 39.8265 | 39.8265 | 39.669 | 40.109
2039-01-01 | 53.4601 |  |  |  |  | 2039-04-01 | 2039-05-01 | 37.2907 | 37.6157 | 37.6157 | 37.4807 | 37.5857 | 36.8332 | 37.1232 | 37.1232 | 37.6032 | 37.6032 | 37.4457 | 37.8857
2039-02-01 | 48.7104 |  |  |  |  | 2039-05-01 | 2039-06-01 | 29.4081 | 29.7331 | 29.7331 | 29.5981 | 29.7031 | 28.9506 | 29.2406 | 29.2406 | 29.7206 | 29.7206 | 29.5631 | 30.0031
2039-03-01 | 39.514 |  |  |  |  | 2039-06-01 | 2039-07-01 | 30.7219 | 31.0469 | 31.0469 | 30.9119 | 31.0169 | 30.2644 | 30.5544 | 30.5544 | 31.0344 | 31.0344 | 30.8769 | 31.3169
2039-04-01 | 37.2907 |  |  |  |  | 2039-07-01 | 2039-08-01 | 34.0568 | 34.3818 | 34.3818 | 34.2468 | 34.3518 | 33.5993 | 33.8893 | 33.8893 | 34.3693 | 34.3693 | 34.2118 | 34.6518
2039-05-01 | 29.4081 |  |  |  |  | 2039-08-01 | 2039-09-01 | 33.3494 | 33.6744 | 33.6744 | 33.5394 | 33.6444 | 32.8919 | 33.1819 | 33.1819 | 33.6619 | 33.6619 | 33.5044 | 33.9444
2039-06-01 | 30.7219 |  |  |  |  | 2039-09-01 | 2039-10-01 | 29.3071 | 29.6321 | 29.6321 | 29.4971 | 29.6021 | 28.8496 | 29.1396 | 29.1396 | 29.6196 | 29.6196 | 29.4621 | 29.9021
2039-07-01 | 34.0568 |  |  |  |  | 2039-10-01 | 2039-11-01 | 32.5409 | 32.8659 | 32.8659 | 32.7309 | 32.8359 | 32.0834 | 32.3734 | 32.3734 | 32.8534 | 32.8534 | 32.6959 | 33.1359
2039-08-01 | 33.3494 |  |  |  |  | 2039-11-01 | 2039-12-01 | 34.2589 | 34.5839 | 34.5839 | 34.4489 | 34.5539 | 33.8014 | 34.0914 | 34.0914 | 34.5714 | 34.5714 | 34.4139 | 34.8539
2039-09-01 | 29.3071 |  |  |  |  | 2039-12-01 | 2040-01-01 | 35.7748 | 36.0998 | 36.0998 | 35.9648 | 36.0698 | 35.3173 | 35.6073 | 35.6073 | 36.0873 | 36.0873 | 35.9298 | 36.3698
2039-10-01 | 32.5409 |  |  |  |  | 2040-01-01 | 2040-02-01 | 53.914 | 54.239 | 54.239 | 54.104 | 54.209 | 53.4565 | 53.7465 | 53.7465 | 54.2265 | 54.2265 | 54.069 | 54.509
2039-11-01 | 34.2589 |  |  |  |  | 2040-02-01 | 2040-03-01 | 49.1239 | 49.4489 | 49.4489 | 49.3139 | 49.4189 | 48.6664 | 48.9564 | 48.9564 | 49.4364 | 49.4364 | 49.2789 | 49.7189
2039-12-01 | 35.7748 |  |  |  |  | 2040-03-01 | 2040-04-01 | 39.8495 | 40.1745 | 40.1745 | 40.0395 | 40.1445 | 39.392 | 39.682 | 39.682 | 40.162 | 40.162 | 40.0045 | 40.4445
2040-01-01 | 53.914 |  |  |  |  | 2040-04-01 | 2040-05-01 | 37.6073 | 37.9323 | 37.9323 | 37.7973 | 37.9023 | 37.1498 | 37.4398 | 37.4398 | 37.9198 | 37.9198 | 37.7623 | 38.2023
2040-02-01 | 49.1239 |  |  |  |  | 2040-05-01 | 2040-06-01 | 29.6578 | 29.9828 | 29.9828 | 29.8478 | 29.9528 | 29.2003 | 29.4903 | 29.4903 | 29.9703 | 29.9703 | 29.8128 | 30.2528
2040-03-01 | 39.8495 |  |  |  |  | 2040-06-01 | 2040-07-01 | 30.9827 | 31.3077 | 31.3077 | 31.1727 | 31.2777 | 30.5252 | 30.8152 | 30.8152 | 31.2952 | 31.2952 | 31.1377 | 31.5777
2040-04-01 | 37.6073 |  |  |  |  | 2040-07-01 | 2040-08-01 | 34.346 | 34.671 | 34.671 | 34.536 | 34.641 | 33.8885 | 34.1785 | 34.1785 | 34.6585 | 34.6585 | 34.501 | 34.941
2040-05-01 | 29.6578 |  |  |  |  | 2040-08-01 | 2040-09-01 | 33.6326 | 33.9576 | 33.9576 | 33.8226 | 33.9276 | 33.1751 | 33.4651 | 33.4651 | 33.9451 | 33.9451 | 33.7876 | 34.2276
2040-06-01 | 30.9827 |  |  |  |  | 2040-09-01 | 2040-10-01 | 29.5559 | 29.8809 | 29.8809 | 29.7459 | 29.8509 | 29.0984 | 29.3884 | 29.3884 | 29.8684 | 29.8684 | 29.7109 | 30.1509
2040-07-01 | 34.346 |  |  |  |  | 2040-10-01 | 2040-11-01 | 32.8172 | 33.1422 | 33.1422 | 33.0072 | 33.1122 | 32.3597 | 32.6497 | 32.6497 | 33.1297 | 33.1297 | 32.9722 | 33.4122
2040-08-01 | 33.6326 |  |  |  |  | 2040-11-01 | 2040-12-01 | 34.5498 | 34.8748 | 34.8748 | 34.7398 | 34.8448 | 34.0923 | 34.3823 | 34.3823 | 34.8623 | 34.8623 | 34.7048 | 35.1448
2040-09-01 | 29.5559 |  |  |  |  | 2040-12-01 | 2041-01-01 | 36.0786 | 36.4036 | 36.4036 | 36.2686 | 36.3736 | 35.6211 | 35.9111 | 35.9111 | 36.3911 | 36.3911 | 36.2336 | 36.6736
2040-10-01 | 32.8172
2040-11-01 | 34.5498
2040-12-01 | 36.0786

## Peak-Off Peak Breakdown
[7 empty] | 24480 | 28128 | 52608 | 46.53% | 53.47%
| Sundays | Saturdays | Holidays | Days | off Peak Days | Peak Days | Peak Hours | Off Peak Hours | Hours | Peak % | Off Peak %
42370 | 5 | 5 | 1 | 31 | 11 | 20 | 320 | 424 | 744 | 0.43011 | 0.56989
42401 | 4 | 4 | 0 | 29 | 8 | 21 | 336 | 360 | 696 | 0.48276 | 0.51724
42430 | 4 | 4 | 0 | 31 | 8 | 23 | 368 | 376 | 744 | 0.49462 | 0.50538
42461 | 4 | 5 | 0 | 30 | 9 | 21 | 336 | 384 | 720 | 0.46667 | 0.53333
42491 | 5 | 4 | 1 | 31 | 10 | 21 | 336 | 408 | 744 | 0.45161 | 0.54839
42522 | 4 | 4 | 0 | 30 | 8 | 22 | 352 | 368 | 720 | 0.48889 | 0.51111
42552 | 5 | 5 | 1 | 31 | 11 | 20 | 320 | 424 | 744 | 0.43011 | 0.56989
42583 | 4 | 4 | 0 | 31 | 8 | 23 | 368 | 376 | 744 | 0.49462 | 0.50538
42614 | 4 | 4 | 1 | 30 | 9 | 21 | 336 | 384 | 720 | 0.46667 | 0.53333
42644 | 5 | 5 | 0 | 31 | 10 | 21 | 336 | 408 | 744 | 0.45161 | 0.54839
42675 | 4 | 4 | 1 | 30 | 9 | 21 | 336 | 384 | 720 | 0.46667 | 0.53333
42705 | 4 | 5 | 1 | 31 | 10 | 21 | 336 | 408 | 744 | 0.45161 | 0.54839
42736 | 5 | 4 | 1 | 31 | 10 | 21 | 336 | 408 | 744 | 0.45161 | 0.54839
42767 | 4 | 4 | 0 | 28 | 8 | 20 | 320 | 352 | 672 | 0.47619 | 0.52381
42795 | 4 | 4 | 0 | 31 | 8 | 23 | 368 | 376 | 744 | 0.49462 | 0.50538
42826 | 5 | 5 | 0 | 30 | 10 | 20 | 320 | 400 | 720 | 0.44444 | 0.55556
42856 | 4 | 4 | 1 | 31 | 9 | 22 | 352 | 392 | 744 | 0.47312 | 0.52688
42887 | 4 | 4 | 0 | 30 | 8 | 22 | 352 | 368 | 720 | 0.48889 | 0.51111
42917 | 5 | 5 | 1 | 31 | 11 | 20 | 320 | 424 | 744 | 0.43011 | 0.56989
42948 | 4 | 4 | 0 | 31 | 8 | 23 | 368 | 376 | 744 | 0.49462 | 0.50538
42979 | 4 | 5 | 1 | 30 | 10 | 20 | 320 | 400 | 720 | 0.44444 | 0.55556
43009 | 5 | 4 | 0 | 31 | 9 | 22 | 352 | 392 | 744 | 0.47312 | 0.52688
43040 | 4 | 4 | 1 | 30 | 9 | 21 | 336 | 384 | 720 | 0.46667 | 0.53333
43070 | 5 | 5 | 1 | 31 | 11 | 20 | 320 | 424 | 744 | 0.43011 | 0.56989
43101 | 4 | 4 | 1 | 31 | 9 | 22 | 352 | 392 | 744 | 0.47312 | 0.52688
43132 | 4 | 4 | 0 | 28 | 8 | 20 | 320 | 352 | 672 | 0.47619 | 0.52381
43160 | 4 | 5 | 0 | 31 | 9 | 22 | 352 | 392 | 744 | 0.47312 | 0.52688
43191 | 5 | 4 | 0 | 30 | 9 | 21 | 336 | 384 | 720 | 0.46667 | 0.53333
43221 | 4 | 4 | 1 | 31 | 9 | 22 | 352 | 392 | 744 | 0.47312 | 0.52688
43252 | 4 | 5 | 0 | 30 | 9 | 21 | 336 | 384 | 720 | 0.46667 | 0.53333
43282 | 5 | 4 | 1 | 31 | 10 | 21 | 336 | 408 | 744 | 0.45161 | 0.54839
43313 | 4 | 4 | 0 | 31 | 8 | 23 | 368 | 376 | 744 | 0.49462 | 0.50538
43344 | 5 | 5 | 1 | 30 | 11 | 19 | 304 | 416 | 720 | 0.42222 | 0.57778
43374 | 4 | 4 | 0 | 31 | 8 | 23 | 368 | 376 | 744 | 0.49462 | 0.50538
43405 | 4 | 4 | 1 | 30 | 9 | 21 | 336 | 384 | 720 | 0.46667 | 0.53333
43435 | 5 | 5 | 1 | 31 | 11 | 20 | 320 | 424 | 744 | 0.43011 | 0.56989
43466 | 4 | 4 | 1 | 31 | 9 | 22 | 352 | 392 | 744 | 0.47312 | 0.52688
43497 | 4 | 4 | 0 | 28 | 8 | 20 | 320 | 352 | 672 | 0.47619 | 0.52381
43525 | 5 | 5 | 0 | 31 | 10 | 21 | 336 | 408 | 744 | 0.45161 | 0.54839
43556 | 4 | 4 | 0 | 30 | 8 | 22 | 352 | 368 | 720 | 0.48889 | 0.51111
43586 | 4 | 4 | 1 | 31 | 9 | 22 | 352 | 392 | 744 | 0.47312 | 0.52688
43617 | 5 | 5 | 0 | 30 | 10 | 20 | 320 | 400 | 720 | 0.44444 | 0.55556
43647 | 4 | 4 | 1 | 31 | 9 | 22 | 352 | 392 | 744 | 0.47312 | 0.52688
43678 | 4 | 5 | 0 | 31 | 9 | 22 | 352 | 392 | 744 | 0.47312 | 0.52688
43709 | 5 | 4 | 1 | 30 | 10 | 20 | 320 | 400 | 720 | 0.44444 | 0.55556
43739 | 4 | 4 | 0 | 31 | 8 | 23 | 368 | 376 | 744 | 0.49462 | 0.50538
43770 | 4 | 5 | 1 | 30 | 10 | 20 | 320 | 400 | 720 | 0.44444 | 0.55556
43800 | 5 | 4 | 1 | 31 | 10 | 21 | 336 | 408 | 744 | 0.45161 | 0.54839
43831 | 4 | 4 | 1 | 31 | 9 | 22 | 352 | 392 | 744 | 0.47312 | 0.52688
43862 | 4 | 5 | 0 | 29 | 9 | 20 | 320 | 376 | 696 | 0.45977 | 0.54023
43891 | 5 | 4 | 0 | 31 | 9 | 22 | 352 | 392 | 744 | 0.47312 | 0.52688
43922 | 4 | 4 | 0 | 30 | 8 | 22 | 352 | 368 | 720 | 0.48889 | 0.51111
43952 | 5 | 5 | 1 | 31 | 11 | 20 | 320 | 424 | 744 | 0.43011 | 0.56989
43983 | 4 | 4 | 0 | 30 | 8 | 22 | 352 | 368 | 720 | 0.48889 | 0.51111
44013 | 4 | 4 | 1 | 31 | 9 | 22 | 352 | 392 | 744 | 0.47312 | 0.52688
44044 | 5 | 5 | 0 | 31 | 10 | 21 | 336 | 408 | 744 | 0.45161 | 0.54839
44075 | 4 | 4 | 1 | 30 | 9 | 21 | 336 | 384 | 720 | 0.46667 | 0.53333
44105 | 4 | 5 | 0 | 31 | 9 | 22 | 352 | 392 | 744 | 0.47312 | 0.52688
44136 | 5 | 4 | 1 | 30 | 10 | 20 | 320 | 400 | 720 | 0.44444 | 0.55556
44166 | 4 | 4 | 1 | 31 | 9 | 22 | 352 | 392 | 744 | 0.47312 | 0.52688
44197 | 5 | 5 | 1 | 31 | 11 | 20 | 320 | 424 | 744 | 0.43011 | 0.56989
44228 | 4 | 4 | 0 | 28 | 8 | 20 | 320 | 352 | 672 | 0.47619 | 0.52381
44256 | 4 | 4 | 0 | 31 | 8 | 23 | 368 | 376 | 744 | 0.49462 | 0.50538
44287 | 4 | 4 | 0 | 30 | 8 | 22 | 352 | 368 | 720 | 0.48889 | 0.51111
44317 | 5 | 5 | 1 | 31 | 11 | 20 | 320 | 424 | 744 | 0.43011 | 0.56989
44348 | 4 | 4 | 0 | 30 | 8 | 22 | 352 | 368 | 720 | 0.48889 | 0.51111
44378 | 4 | 5 | 1 | 31 | 10 | 21 | 336 | 408 | 744 | 0.45161 | 0.54839
44409 | 5 | 4 | 0 | 31 | 9 | 22 | 352 | 392 | 744 | 0.47312 | 0.52688
44440 | 4 | 4 | 1 | 30 | 9 | 21 | 336 | 384 | 720 | 0.46667 | 0.53333
44470 | 5 | 5 | 0 | 31 | 10 | 21 | 336 | 408 | 744 | 0.45161 | 0.54839
44501 | 4 | 4 | 1 | 30 | 9 | 21 | 336 | 384 | 720 | 0.46667 | 0.53333
44531 | 4 | 4 | 1 | 31 | 9 | 22 | 352 | 392 | 744 | 0.47312 | 0.52688